## Slide 1: Presentation Outline
Common Terms / Concepts
HVAC Building Blocks
  Plant Level Building Blocks
    Description / Application Data
    Green opportunities
    Selection Criteria
  Air Distribution Building Blocks
    same
  Zone Building Blocks
    Same
Links

## Slide 2: “Energy”
“Energy” is defined as the ability to do work Units of energy:
BTU (the amt. of heat required to raise the temperature of 1 lb. of water by 1°F)
970 BTU is the latent heat of evaporation of water, or, the amount of heat energy required to evaporate 1 lb of water.
WATT HOUR (= BTU / 3.413)
THERM (= 100,000 BTU)

## Slide 3: “Power”
“Power” is the measurement of how much work is accomplished in a specific amount of time.
Units of Power:
BTUH (same as BTUs per Hour)
WATTS = BTUH ÷ 3.413
TON = 12,000 BTUH = the energy it takes to melt 2,000 lbs. of ice @ 32 deg F in 24 hours
HORSEPOWER = 2540 BTUH = 746 WATTS

## Slide 4: Heat Transfer Terms

## Slide 5: Psychrometrics air properties and their interrelationships

## Slide 6
HVAC System Building Blocks
Refrigeration Plant
Air Distribution System
Zone Control

## Slide 7: Refrigeration System Function
Use Energy Input
to
Remove Heat (cooling) from a (Lower Temperature) Space
and
Reject that Heat (heating) to a (Higher Temperature) Space.

## Slide 8
Cooling Efficiency
EER = space cooling effect (in BTUH) power input (in Watts)
High Efficiency means more cooling effect for less power input

## Slide 9: Efficiency Expressions
EER = BTUH cooling output ÷ Watts input
SEER = BTUH cooling output ÷ Watts input averaged over normal annual usage period
COP = BTUH output ÷ BTUH input
EIR = BTUH input ÷ BTUH output
KW / Ton = KW input ÷ Tons cooling output
IPLV = Integrated Part Load Value = a standard formula that takes part load efficiencies into account

## Slide 10: Refrigeration Cycle
Condenser
Space heat and Compressor Heat to Outside
Expansion Valve
Compressor
High Temp, High Pressure Gas
Low Temp, High Pressure Liquid
Low Temp,
High Temp, Low Pressure Gas
Evaporator
Energy into the system
Low Pressure Liquid
Cooling Effect (heat out of the conditioned space)

## Slide 11: Refrigeration System Building Blocks All Refrigerant Systems Have These Pieces in Various Boxes In Various Locations
Condenser:
  High Pressure Refrigerant Gas releases heat and condenses and becomes refrigerant liquid (phase change)
Expansion Valve
  High pressure liquid refrigerant expands and becomes low pressure liquid
Evaporator
  Low pressure refrigerant liquid picks up heat and evaporates and becomes refrigerant gas (phase change)
Compressor
  Low pressure refrigerant gas is compressed with power input and and becomes high pressure refrigerant gas

## Slide 12: Heat Pump Operation Reversed Refrigerant Flow
Evaporator: Removes Heat from Outdoor Air
Bi-Directional Expansion Valve
Compressor
Condenser: Rejects heat to conditioned space
Power into the system

## Slide 13: Refrigeration System Selection Factors
How many tons is my project?
Cost Goals?
EFFICIENCY GOALS
What are my outdoor limitations?
  Weight
  Roof space
  Property line acoustics
What are my indoor limitations?
  Floor space
  Ceiling space
  Access to outdoor air
24/7 Operation?

## Slide 14: Refrigeration Plant Green Opportunities
Non-HCFC Refrigerant Types
Ground or Lake as a Heat Source and Sink
Equipment Efficiency Improvement
– Full Load and Part load
Equipment Right Sizing
Pump Energy Reductions
Larger Cooling Tower for Lower Condenser Water Temperatures
Larger heat transfer areas
Optimized operation
Temperature resetting
Heat Recovery Options
Natural Ventilation or Mixed Mode Ventilation
Direct Evaporative Cooling (Swamp Cooling)
Evaporative Condensing

## Slide 15: Air Cooled Split System ACU or Heat Pump
Condenser Coil & Fan
Compressor
High Temp, Low Pressure Gas
Low Temp, High Pressure Liquid
Expansion Valve Evaporator Evaporator Fan
Split System DX Fan Coil (Indoor)
Split System Condensing Unit (Outdoor)

## Slide 16: Air Cooled Split System
Typical Equipment Designation
  Direct Expansion Fan coil & Condensing Unit (DXFC & CU)
Air Distribution via indoor DXFC
Typical Heating Sources
  Heat Pump, Electric, Hot Water, Gas Furnace
Typical Applications
  Single Family Residences
  Retail
  24/7 isolated cooling space (server rooms)
Limitations: Typical proximity indoor/outdoor requirement is 75’
Costs: $4,000/ton complete

## Slide 17: Air Cooled Split System 10 – 80 Tons
Often called “Air Cooled Vertical Self Contained Units”
Evaporator
Condenser Coil & Fan
Expansion Valve Compressor
Low Temp, High Pressure Liquid
Evaporator Fan
Indoor Vertical Self Contained ACU or Computer Room ACU
Air Cooled Condenser (Roof, Garage, outside)
High Temp, High Pressure Gas

## Slide 18: Air Cooled Split System (10 – 80 tons)
Typical Equipment Designation
  Vertical Self-Contained Units & Condensing Unit (ACU & CU) or (VSC & CU)
  Computer Room Air-Conditioning Unit (CRAC)
Air Distribution via indoor VSC, CRAC, or ACU
Typical Heating Sources
  Heat Pump, Electric, Hot Water
Typical Use
  Data Center
  Office VAV or CAV
Limitations: Typical proximity indoor/outdoor requirement is 75’; floor space required
Costs: $8,000/ton complete

## Slide 19: Package Rooftop: Air-Cooled DX ACU or Air Source Heat Pump
Evaporator Coil
Condenser
Compressor
Evaporator Fan
Outdoor Unit
Expansion Valve

## Slide 20: Package Rooftop Air-Cooled DX
Typical Equipment Designation
  Air-conditioning Unit (AC)
  Rooftop Unit (RTU)
Air Distribution via outdoor AC or RTU
Typical Heating Sources
  Heat Pump, Electric, Hot Water, Gas Furnace
Typical Applications
  Office VAV or CAV
  Retail
Limitations: Standard Units come in 2 – 130 tons; Air is shafted down to floors.
Costs: Equipment only $1,000/ton installed; total system S&C $10/sf.

## Slide 21: Water Cooled Air-Conditioning Unit
Expansion Valve
Evaporator Compressor
Evaporator Fan
Water Cooled DX ACU (Indoors typically)
Condenser Barrel
Condenser Water Return 86°F
Condenser Water Supply 76°F
Cooling Tower

## Slide 22: Water Cooled Air-Conditioning Unit
Typical Equipment Designation
  Air-conditioning Unit & Fluid Cooler (ACU & FC)
  Vertical Self-Contained & Fluid Cooler (VSC & FC)
Air Distribution via indoor ACU or VSC
Typical Heating Sources
  Electric, Hot Water
Typical Applications
  Office VAV or CAV
  Retail
Limitations: Standard Units come in 30 – 80 tons; Mechanical Room required
Costs: Equipment only $2,500/ton installed; total system S&C
$12/sf.

## Slide 23: Water Source Heat Pumps “2 Pipe System”
Evaporator or Condenser Coil
Bi Directional Expansion Valve
Compressor
Evaporator or Condenser Fan
Water Source Heat Pump Indoor
Closed Circuit Fluid Cooler Outdoor
Condenser or Evaporator Barrel
Condenser Water Return 86°F Max
Condenser Water Supply 60°F Min
Boiler

## Slide 24: Water Source Heat Pump
Typical Equipment Designation
  Water Source Heat Pump & Fluid Cooler (WSHP & FC)
  Heat Pump & Fluid Cooler (HP & FC)
Air Distribution via indoor WSHP or HP
Typical Heating Sources
  Gas boiler
Typical Applications
  Residential
  Retail
  24/7 isolated cooling areas less than 5 tons
Limitations: Non – Residential Energy Codes limit usage by requiring air side economizer
Costs: $13,000/WSHP

## Slide 25: Air Cooled Chiller
Chilled Water Supply
42°F
Evaporator Barrel
Expansion Valve
Condenser Coil & Fan
Compressor
Air Cooled Chiller (outdoor)
Evaporator Fan
Chilled Water Air Handler or Fan Coil (indoor)
Chilled Water Return 56°F

## Slide 26: How Many Pipes?
“2 Pipe System”
  Water Source Heat Pumps
    Condenser Water Supply
    Condenser Water Return
    Gas Boiler at the Roof
“2 Pipe System”
  Chilled Water Fan Coils
    Chilled Water Supply
    Chilled Water Return
    Electric Heat at each Fan Coil
“4 Pipe System”
  Chilled Water / Hot Water Fan Coils
    Chilled Water Supply
    Chilled Water Return
    Hot Water Supply
    Hot Water Return

## Slide 27: Air Cooled (Water) Chiller
Typical Equipment Designation
  Air-cooled Water Chiller (ACWC)
  Air-cooled chiller (ACC)
Air Distribution via indoor or outdoor chilled water air-handling unit (AHU) or fan coil (FC)
Typical Heating Sources
  Hot water, electric
Limitations: Tonnage from 30 – 500; takes up a lot of space outdoors and is heavy.
Costs: Equipment only installed $600/ton; Total S&C $14/SF

## Slide 28: Water Cooled Chiller Plant with AHU
Condenser Water Supply 76°F
Evaporator Barrel
Expansion Valve
Compressor
Water Cooled Chiller
Chilled Water Air Handler or Fan Coil
Chilled Water Supply 42°F
Condenser Barrel
Condenser Water
Return 86°F
Cooling Tower
Chilled Water
Return 56°F

## Slide 29: Water Cooled Chiller
Typical Equipment Designation
  Chiller (CH) and Cooling Tower (CT)
Air Distribution via indoor or outdoor chilled water air-handling unit (AHU) or fan coil (FC)
Typical Heating Sources
  Hot water, electric
Typical Applications
  Office VAV or CAV
  High Rise
  Biotech, Hospital
  24/7 isolated cooling areas less than 5 tons
Limitations: CH Needs to be indoor; they are noisy
Refrigeration Machinery Room needed
Costs: Equipment only installed $1000/ton; Total S&C $15/SF

## Slide 30: Ground Source Heat Pump
Evaporator or Condenser Coil
Bi Directional Expansion Valve
Compressor
Evaporator or Condenser Fan
Water Cooled Heat Pump
Condenser or Evaporator Barrel
Condenser Water Return 86°F Max
Condenser Water Supply 60°F Min
Wells, direct buried loops, lake loops
Auxiliary boiler or fluid cooler could be needed

## Slide 31: Ground Source Heat Pump
Typical Equipment Designation
  Water Source Heat Pump (WSHP)
  Heat Pump (HP)
Air Distribution via indoor WSHP or HP
Typical Heating Sources
  Hot Water
Typical Applications
  Residential
  Retail
  24/7 isolated cooling areas less than 5 tons
Limitations: Energy Codes limit usage
Costs: $17,000/WSHP

## Slide 32: Air Distribution Building Blocks
Outdoor Air Intake Location
AHU or ACU Location(s)
Return Air Path (Ducted or plenum)
Return Fans or Barometric Relief or Relief Fan
Relief Air Location

## Slide 33: Air Distribution Green Opportunities
Underfloor Air Distribution
VAV or fans with VFDs
Low Supply Air Temperature Delivery
Temperature reset to maximize economizer hours
CO2 Control Ventilation
Watts/cfm Strategies
Low VOC Duct Sealant
Natural Ventilation
Heat Recovery
Mixed Mode or Natural Ventilation

## Slide 34: Air Distribution Selection Criteria
How much air (cubic feet/minute (CFM)) is required?
How many Zones?
Cost Goals?
Outdoor limitations?
  Weight
  Roof space
What are my indoor limitations?
  Floor space
  Ceiling space
  Access to outdoor air
Are there spaces with different operating hours (Office, Retail, 24/7 Operation)?
Are there air streams from spaces that should not be recirculated into other spaces?

## Slide 35: Central Air Handlers or ACU’s (air cooled DX, water cooled DX, chilled water, direct evaporative cooling, etc.)
Coordinate Shaft Area
Attenuate noise large central unit
No louvers required
Coordinate GC built 4’ tall roof curb

## Slide 36: Floor by Floor Air Handlers or ACU’s (water cooled or chilled water)
Coordinate Floor area for mechanical rooms
Attenuate noise from mechanical room
No vertical shafts required
Intake louvers required
Exhaust louvers required

## Slide 37: Airside Economizer
Outside Air Percentage
Supply air is a mix of two sources:
  Return Air
  Outside Air
Outside air economizer operation in a nutshell:
  Use the coolest source air to maximize cooling without the use of refrigeration

## Slide 38: Airside Economizer Code Rules of The Road
Baseline code requires airside economizer on all air systems
Exceptions:
  Seattle
    Efficiency 10% better than code
      4.5 ton max size and a total max capacity of 5% of airside economizer capacity
    Efficiency 15% better than code (server rooms only)
      No size or quantity limit
  WA State
    Efficiency 10% better than code
      No size limit
      Total max capacity of 20% of airside economizer capacity

## Slide 39: Ceiling Space Coordination

## Slide 40: Zone Building Blocks
Temperature Sensors
Supply Air Diffusers
Return Air Grilles
Manual Volume Dampers
VAV Boxes
Zone Heating or Cooling Coils

## Slide 41: Zone Green Opportunities
Underfloor Air Distribution
VAV boxes with ECM motors
CO2 Control Ventilation
Watts/CFM Strategies
Fan boxes using return air as first stage of heat
Hot Water heating coils?
Radiant Heating
Natural Ventilation

## Slide 42: Zone Selection Criteria
What occupancies do I have?
How many different occupancies or ZONES do I have?
What level of control is appropriate?
Cost Goals?
What is my heating source?
Is this system exposed?
Areas with special HVAC needs? Temp, Humidity, filtration, hours of operation?

## Slide 43: VAV Systems
Variable Air Volume (VAV)
Series boxes (VAV)
Parallel Boxes (VAV)
Pinch Boxes (VAV)

## Slide 44: VAV Terminal Type: Pinch Box
Also known as “Single Duct boxes”, “Squeeze boxes”, “Reheat boxes”
  Maximum allowed air quantity in heating is the amount req’d for ventilation purposes (except for labs or hospitals)
  Electric heaters: max delta T is approximately 40°F
  Diffusers rule of thumb; do not reduce airflow to less than ½ of design during heating.

## Slide 45: VAV Terminal Types: Fan Boxes
Series Fan VAV Box
Fan in series with air valve
Runs continuously
Allows low temperature primary air
Parallel Fan VAV Box
Fan in parallel with air valve
Runs during heating only

## Slide 46: Indoor Air Quality
Human Effluent
  CO2
Materials Effluent
  VOC’s
  Etc
ASHRAE 62.1 Ventilation
  (# people x _cfm/ person) +
  (area x _cfm / square foot)

## Slide 47: Selection Scorecard

## Slide 48: Life Cycle Costing – Buying the Best Value
First Cost Constraints
Operational Costs Energy Maintenance Repairs
Flexibility to Avoid Future Change Costs (TI)
Replacement Horizon
Equipment Life – Planned & Engineered Replacement Strategies

## Slide 49: Links for HVAC Basics
http://www.hpac.com/
http://www.esmagazine.com/
http://www.ashrae.org/
http://www.usgbc.org/
http://www.air-conditioner-selection.com/air- conditioning-articles.html
http://www.seattle.gov/dpd/
http://www.sbcc.wa.gov/sbccindx.html

## Slide 50: Teamwork = Results
Go team

## Slide 51: Thank You