## Slide 1: Title page
By: Steve Ward
Filter-Driers

## Slide 2: Today’s Topics
Parker Hannifin - the Company
Filter Driers for HVACR Industry

## Slide 3: Parker Diversity

## Slide 4: Parker Corporate Overview
Filtration
Seal
Aerospace
Automation
Instrumentation
Hydraulics
Fluid Connectors
Sporlan
Washington, MO (3)
Greenfield, TN (1)
Owensville, MO (2)

## Slide 5: Filter Driers
A Drier in a HVACR system has two Functions:
  To adsorb system contaminants (water & acid).
  To provide physical filtration.

## Slide 6: Contaminates
Foreign Matter
Acid
Moisture
Sludge & Varnish
Wax

## Slide 7: Contaminants
Contaminant Types
Anything circulating in the system other than refrigerant and oil
Contaminants introduced or generated in a system:
  From installation or service
  From adverse operating conditions
Acid Moisture Foreign Matter Wax Sludge & Varnish

## Slide 8: Contaminants
Lubricant – reacts with moisture to form acid
Refrigerant – reacts with moisture to form acid
Moisture – causes copper plating and corrosion
Water or Moisture

## Slide 9: Foreign Matter
Oxide Scale – Dirt – Metallic Particles – Sludge – Flux
Damages compressor components
Affects valve operation
Plugs capillary tubes
POE lubricant suspends and circulates large amounts of debris

## Slide 10: Wax
Wax-like substances
Potential sources:
  Excessive brazing paste
  Manufacturing processes
    Cutting lubricants
    Corrosion inhibitors
    Drawing compounds
  Rubber Hoses

## Slide 11: Sludge and Varnish
By-product of mineral and alkylbenzene Oil breakdown:
  Varnish – Sludge – Carbonaceous powder
  Ranges from residues at TXV to beige/black/gray solids captured in the filter-Drier
POE lubricant is more thermally stable; but hydrolytic (reacts with water) to form acid.

## Slide 12: Solution
Install a Filter-Drier
  Must remove a variety of contaminants
  Must be compatible with today’s refrigerants and lubricants

## Slide 13: Filter-Driers
Drier Selections:
  Type of System.
  Connections.
  Suction or Liquid Line.
  Flow Capacity (size of system).
  Refrigerant Type.
  Construction Material.
  Safe Working Pressure.

## Slide 14: Driers / Desiccants
A Desiccant is a substance that adsorbs water and is used to remove moisture and acid.
  The three most commonly used desiccants are:
Silica Gel
Activated Alumina
Molecular Sieve

## Slide 15: Silica Gel
Silica gel is a non-crystalline material with a molecular structure formed by bundles of polymerized silica (SiO2).
Gel-type desiccants utilize weak bonds formed between water and the desiccant.
Silica gel is not widely used in today’s filter Driers.

## Slide 16: Activated Alumina
Activated alumina is formed from aluminum oxide (Al2O3) and is not a highly crystalline material.
Water
Organic Acid

## Slide 17: Activated Alumina
High Acid Capacity
Low Water Capacity

## Slide 18: Molecular sieves
These are crystalline sodium alumino-silicates (synthetic zeolites) having cubic crystals, which selectively adsorb molecules based on molecular size and polarity.
One of the keys to molecular sieve is its ability to remove water from refrigerant at low parts per million (ppm) level.

## Slide 19: Molecular sieves
High Water Capacity
Low Acid Capacity

## Slide 20: Desiccant / Dry Down
Molecular Sieve
Activated Alumina
Silica Gel
Water in Refrigerant, ppm by weight
Water capacity, weight %
0 10 20 30 40
5
10
15
20

## Slide 21: Desiccants
Desiccants are available in granular, bead, and block forms. Solid core desiccants, or block forms, consist of desiccant beads, granules, or both, held together by a binder. The binder is usually a non-desiccant material.
Beaded molecular sieve desiccants offer higher water capacity per unit mass than solid core desiccants.
Due to the dense nature of cores, core Driers usually have a higher pressure drop than comparable loose filled Driers.

## Slide 22: Liquid Line Filter Driers
Designed for use in Liquid Lines.
Compatible for use with all commercially available refrigerants including R-410A.
Compatible with Mineral, Alkylbenzene or POE oils.
Spring load molecular sieve and activated alumina.
Solid copper ODF or Nickel plated steel SAE fittings.
Powder coat exterior paint exceeds 500 hrs. salt spray test.
3 Cubic In. through 75 Cubic In. (Flare or ODF)
Gold Label LLD Series

## Slide 23: Liquid Line Filter-Drier
Baffle Plates
Spring Loaded
Multi-layered filtration
Compacted Dessicant Bead
FLOW
Steel Shell
Solid Copper fittings

## Slide 24: Liquid Line Filter Driers
Moisture / Liquid indicator combined with Gold Label LLD
Available in popular 083S and 163S sizes
Solid Copper Fittings
Replaceable Indicator Element
Reduce Leaks and Installation Costs
DSG Filter-Drier Sightglass

## Slide 25
SS Series Overview
Maximum Rated Pressure: 650 psi
R-410A Capable
High Contaminant Capacity
New Design:
Spherical shape reduces shell wall thickness
Core fills shell with similar desiccant load as prior Sahara Series design but in smaller size
Shape reduces pressure drop
Excellent combination of solid debris capture capability and water capacity
Recognized Parker Brand
2
Made in North America
3
Compact Core Style Model
1
Unique Selling Features
Notes: Really should be titled “hydrocarbon optimized”
Water Capacity
Water capacity at a 50 ppm dryness level for R-290 at 125 deg F is 30 drops
Burst pressure of 2500 psi which at a minimum allows a 500 psig MRP

## Slide 26: SS Series
Recommended Application
  AC only
  Gold Label LLD for Refrigeration Applications
Literature
  Catalog A-1 (Parker)
    Performance data
    Dimensional information
    Recommended Tonnage Table
Recommended Tonnage | Model | Nominal Size
2 | 2SS3S | 04
3 | 3SS3S | 08
5 | 5SS3S | 16
5SS3S
Recommended Tonnage
Series Description
Connection Size and Type – 3/8” Solder

## Slide 27: Suction Line Filter Driers
Designed for system clean-up.
Solid Core filter driers for use in the suction line.
The Core material collects and holds a maximum amount of contaminants with a minimum pressure drop.
Contaminants include acids and other harmful particles that may be present after a motor burn-out.
Access valves on both sides of the filter allow easy measurement of pressure drop through the filter.
8 Cubic In. through 54 Cubic In. (Flare or ODF)
Gold Label SLD Series

## Slide 28: Suction Line Filter Driers
Designed for A/C system clean-up
Low pressure drop
High acid capacity
Solid copper ODF connections 5/8”, 3/4” or 7/8”
Access valve on the filter allow easy measurement of pressure drop through the filter.
Available in 16 and 30 Cubic In. sizes
Sahara SLD Series

## Slide 29: Steel Bi-Flow Filter Driers
The “BF” Series bi-flow Drier is designed specifically for heat pump application.
Desiccant core provides removal of solid contaminants, acid and moisture.
Solid copper ODF or Nickel plated steel SAE fittings
Core is cushioned for protection.
Powder coat exterior paint exceeds 500 hrs. salt spray test.
Available in 8, 16, and 30 Cubic In. (Flare or ODF)
Gold Label BF Series

## Slide 30: SSBF Series
Recommended Application
  HP only
  Gold Label BF for Refrigeration Applications
Literature
  Catalog A-1 (Parker)
    Performance data
    Dimensional information
    Recommended Tonnage Table
Recommended Tonnage | Model | Nominal Size
3 | 3SSBF3S | 08
5 | 5SSBF3S | 16
5SSBF3S
Recommended Tonnage
Series Description
Connection Size and Type – 3/8” Solder

## Slide 31: Bi-directional Flow and Filtration
Bi-Flow Drier

## Slide 32: Bi-directional Flow and Filtration
Cooling Mode

## Slide 33: Bi-directional Flow and Filtration
Heating Mode

## Slide 34: Bi-directional Flow and Filtration

## Slide 35: What about the numbers?
The first two numbers indicate the Drier size.
032 is 3 cubic inch
053 is 5 cubic inch
084S is 8 cubic inch
165 is 16 cubic inch
307S is 30 cubic inch
415 is 41 cubic inch
759S is 75 cubic inch
The last number indicates the connection in 8’ths.
032 is a 2/8" or 1/4" SAE flare
053 is a 3/8" SAE flare
084S is a 4/8" or 1/2" Sweat
165 is a 5/8" SAE flare
307S is a 7/8" Sweat
759S is a 9/8" or 1-1/8”Sweat
When an alphabetical letter follows such as 759S it identifies the Drier as having a Sweat Connection (ODS).

## Slide 36: Bi-directional Flow and Filtration

## Slide 37: Filter Driers
Questions?