## Slide 1: Parker Hannifin Corp.
By:

## Slide 2: Today’s Topics
Parker Hannifin
- the Company
Solenoid Valves
Steam & Hot
Water Valves
NATE Certified for Continuing Education Credit

## Slide 3: Parker Diversity

## Slide 4: Parker Corporate Overview
Filtration
Seal
4
Aerospace
Hydraulics
Fluid Connectors
Automation Instrumentation
Sporlan
Washington, MO (3) New Haven, IN (1) Greenfield, TN (1)
Owensville, MO (2)

## Slide 5: Solenoid Valves
A solenoid valve is...”
An electromechanical control
of flow.
Operated by magnetic flux that moves a magnetic plunger or lever away from or towards an orifice.

## Slide 6: Coils / Magnetic Lines

## Slide 7: Solenoid Valves Design Type
Pilot Operated -
“differential pressure across the orifice is required to open and close the main orifice”
Direct Acting -
“the main orifice is opened and closed by the plunger”
Hung Diaphragm -
“the main orifice is controlled by a diaphragm assembly that is mechanically connected to the plunger”
Direct Acting
Pilot Operated Hung Diaphragm

## Slide 8: Normally Closed - Direct Acting Not energized / Closed
Coil
Body
Body materials available in various metals
Orifice / Port
restricts or limits flow through valve
Return Spring
Sleeve
flange & stop carry magnetic flux
Plunger Assembly
seal materials
selected for media
compatibility

## Slide 9: Normally Closed - Direct Acting Energized / Valve Open

## Slide 10: Normally Closed - Pilot Operated Coil Not Energized / Valve Closed
Plunger
Coil
Diaphragm
Pilot Orifice
Body
Sleeve
flange & stop carry magnetic flux
Equalizer Orifice
Return
Spring

## Slide 11: Normally Closed - Pilot Operated Coil Energized / Valve Opening

## Slide 12: Normally Closed - Pilot Operated Coil Energized / Valve Open and Operating

## Slide 13: Normally Closed - Pilot Operated Coil Not Energized / Valve starts to Close

## Slide 14: Normally Closed - Pilot Operated Coil Not Energized / Valve Closed

## Slide 15: Normally Closed - Hung Diaphragm Coil Not Energized – Valve Closed
Pilot Orifice
Diaphragm
Plunger
Coil
Body
Sleeve
flange & stop carry magnetic flux
Equalizer Orifice
Return Spring

## Slide 16: Normally Closed - Hung Diaphragm Coil Energized / Valve starts to Open

## Slide 17: Normally Closed - Hung Diaphragm Coil Energized / Valve Open and Operating

## Slide 18: Normally Closed - Hung Diaphragm Coil Not Energized / Valve starts to Close

## Slide 19: Normally Closed - Hung Diaphragm Coil Not Energized / Valve Closed

## Slide 20: Solenoid Valve - Coils
Uniform layer of copper insulated magnet
wire.
Rated for specific voltage
or range of voltages
Enclosure Carries Magnetic Flux
Coil generates heat when on continuously

## Slide 21: Solenoid Valve - Coils
Standard in HVACR is the Junction Box
Junction Box
Leads
1/2” Conduit
Spade
DIN

## Slide 22: Applications
Frozen Beverage Dispensers
Ice Dispensers Chillers Compressors
Mobile Air Conditioning Units Commercial Air Conditioning Units Mobile Refrigeration Systems Supermarket Racks
Supermarket Cases
Refrigeration Reclaim Units

## Slide 23: Applications - Refrigeration
Compressor Unloaders
Refrigerant Recovery
General
Refrigeration
Humidifiers

## Slide 24: Sizing Valves for HVACR
Size Valves independently for: |  | 
Liquid Line | Hot Gas Line | Suction Line
Refrigerant Phase Matters!

## Slide 25: Solenoid Valves – Capacity Table
Nominal Capacity Ratings
Liquid Capacity based on 40°F Evaporator, 10°F superheat temperature, 100°F condenser temperature and PD across valve: 2 psi for R-134a; 3 psi for R-22, 404A, and 507; 5 psi for R-410A
Suction vapor capacity based on 40°F evaporator temp. + 25°F superheat temp., 100°F condenser, 1 psi PD across valve. Hot Gas capacity based on 40°F evaporator temp. + 25°F superheat temp., 100°F condenser, 2 psi PD across valve.

## Slide 26: HVACR Solenoid Valve Nomenclature
Normally Closed
12
16
22
26
32
36
38
42
46
52
56
Family
Normally Open
-
-
- 27
33
37
39
43
47
53
57
R -
Refrigeration
Type
Size of Conn.
measured in 1/8th of inch E - Ext End F - Flare
Connection
Size of Port
measured in 1/32 of inch Example:
2 = .075”
3 = .101”
6 = 3/16”
9 = 9/32”
Port Size
M
Optional Manual Stem
Example: To order a 2-way normally closed valve, 1/2 ODF connection, manual bypass option, R22, 5 ton liquid line rating, reference R22 valve catalog page. Select R26E64M.

## Slide 27: Electrical Nomenclature – R12 - R57
PKC-1 OPKC-1 PKC-2 OPKC-2
Coil Type
J
J J J J
Enclosure
A A A A A
Insulation Type
Electrical Enclosures – R42 thru R57
Example: To order a junction box coil assembly for R52 , Select PKC-1 208-240/50-60 JAN
Order separate or with valve = R52E359 + 208-240/50-60 JAN
24/50-60
120/50-60
120-240/50-60
208-240/50-60
24 VDC
Voltage
Q (Orange)
M (Blue) N (Red) K (Black) K (Black)
Lead Wire Color Code
Coil Wattage – (O)PKC-1 = 10W, (O)PKC-2 = 15W

## Slide 28: Solenoid Valves
R32E94M w/ PKC-2
2013
R26E64M w/ PKC-1
R12E22 w/ PKC-1
R52E3511 w/ PKC-1
R42E197M w/ PKC-2
R46E259M w/ PKC-2

## Slide 29: Solenoid Valve Coils 2013
Coil Model N/C | Coil Watts | Coil Model N/O | Coil Watts
PKC-1-24 | 10 | OPKC-1-24 | 10
PKC-1-120 | 10 | OPKC-1-120 | 10
PKC-1-120/240 | 10 | OPKC-1-120/240 | 10
PKC-1-208/240 | 10 | OPKC-1-208/240 | 10
PKC-1-24DC | 15 |  | 
PKC-2-24 | 15 | OPKC-2-24 | 15
PKC-2-120 | 15 | OPKC-2-120 | 15
PKC-2-120/240 | 15 | OPKC-2-120/240 | 15
PKC-2-208/240 | 15 | OPKC-2-208/240 | 15
PKC-2-24DC | 18 |  | 
Electrical Enclosures - R12 thru R56

## Slide 30: Solenoid Valves 2013
Valve Series * | Nominal Capacity •‚  |  |  |  |  |  |  |  | NC Coil Junction Box | NO Coil Junction Box
 | Liquid |  |  |  | Hot Gas |  |  |  |  | 
 | R-22 | R-410A | R-134a | R-404A | R-22 | R-410A | R-134a | R-404A |  | 
 |  |  |  | R-507 |  |  |  | R-507 |  | 
R12 E2 | 0.8 | 0.98 |  | 0.53 |  |  |  |  | PKC-1 | xx
R16 E3 | 1.6 | xxx | 1.2 | 1.1 | 0.24 | xxx | 0.20 | 0.22 | PKC-1 | xx
R16 F3 | 1.6 | xxx | 1.2 | 1.1 | 0.24 | xxx | 0.20 | 0.22 | PKC-1 | xx
R22 E5 | 2.8 | 3.45 | 2.1 | 1.9 | 0.45 |  | 0.37 | 0.4 | PKC-1 | xx
R26/27 E6 | 4.9 | 6.02 | 3.8 | 3.3 | 0.84 |  | 0.7 | 0.75 | PKC-1 | OPKC-1
R32/33 E9 | 8.1 | 9.86 | 6.2 | 5.4 | 1.35 |  | 1.12 | 1.21 | PKC-2 | OPKC-2
R36/37 E10 | 11.1 | 13.6 | 8.5 | 7.23 | 1.83 |  | 1.52 | 1.64 | PKC-2 | OPKC-2
R38/39 E14 | 15.8 | 19.2 | 12.0 | 10.4 | 2.62 |  | 2.17 | 2.34 | PKC-2 | OPKC-2
R42/43 E19 | 24.2 | 29.7 | 18.4 | 16.0 | 3.43 | 4.71 | 3.26 | 3.53 | PKC-2 | OPKC-2
R46/47 E25 | 41.4 | 50.6 | 31.5 | 27.4 | 6.74 | 8.07 | 5.60 | 6.04 | PKC-2 | OPKC-2
R52/53 E35 | 57.6 | 57.6 | 53.0 | 38.1 | 9.90 | 12.0 | 8.10 | 9.03 | PKC-1 | OPKC-1
R56/57 E42 | 98.2 | 98.2 | 76.7 | 65.8 | 21.0 | 25.1 | 17.4 | 18.8 | PKC-2 | OPKC-2
* Reference individual catalog pages for specific valve numbers and connection sizes.
 Nominal capacities are based on ARI Standard 760 under the following system conditions:
Liquid line capacities are based on 40°F evaporator, 10°F superheat and 100°F condenser temperatures and pressure drop across valve: 2 psi for R134a - 3 psi for R22, R404A, R507 - 5 psi for R410A
Rated hot gas capacities based on 40°F evaporator temperature plus 25°F superheat and 100°F condenser temperature and 2 psi drop.
For capacities at other ratings, refer to Extended Capacity tables in Parker Catalog D-1.

## Slide 31: Solenoid Valve
Questions?

## Slide 32: Parker Hannifin Corp.

## Slide 33: Steam & Hot Water Valves
1/4” Connections to 1-1/2” NPT
Connections
CV’s from .5 to 22.5
Normally Closed or Normally Open
Ethylene Propylene Seals
Available with variety of Coils &
Voltages
Temperature range 353°F Max.
Hung Diaphragm construction
Springs and Plunger are Stainless Steel

## Slide 34: Normally Closed – Hung Diaphragm Coil Not Energized – Valve Closed
Pilot Orifice
Diaphragm
Plunger
Coil
Body
Sleeve
flange & stop carry magnetic flux
Equalizer Orifice
Return Spring

## Slide 35: Steam & Hot Water Valves
Parker solenoid valves for hot water and steam are two-way valves with one inlet and one
outlet connection.
  Normally closed valves are open when energized.
  Normally open valves are
closed when energized.

## Slide 36: Steam & Hot Water Valves
Wide Variety of Applications
Dry Cleaning
Sterilizers
Steam Irons
Laundry equipment
Steam baths
Moldings
Autoclaves
Steam atomization

## Slide 37: Nomenclature for Steam Valves
08
F
S3
2
40 ACF
Construc- tion
Hung
Body Material
2 = Brass
Operation
C =
Normally Closed
O =
Normally Open
C
Conn. Type
F = Female S = Steam
Pipe Thread 3 = Diaphragm
NPT
Connection Size
Size of end
connection in sixteenths (inches)
Example: 04 = 1/4”
06 = 3/8”
08 = 1/2”
12 = 3/4”
16 = 1”
20 = 1-1/4”
24 = 1-1/2”
Steam Service
40 = Valve
orifice
diameter in
1/64”
increments.
Example: 32 = 1/2”
40 = 5/8”
48 = 3/4”
ACF =
Current Design Series
Coils Ordered Separately
3
Trim
3 = EPDM
Ethylene propylene elastomers

## Slide 38: Steam & Hot Water Valve - Selections

## Slide 39: Steam & Hot Water Valve
Questions?