## Slide 1: Thermostatic Expansion Valves
Presented by: Steve Ward
Thermostatic
Expansion Valves

## Slide 2: Today’s Topics
Parker Hannifin Corp.
Back to Basics
Thermostatic Expansion Valves

## Slide 3: Parker History
1918
1930’s
2001
2004
2005
2010
The Parker Appliance Company Founded by Arthur LaRue Parker
The Company grows while serving a booming auto industry and fledging aircraft pioneers.
1920’s
Parker sales reach 8 million.
Parker Appliance acquires the Hannifin Company (industrial fluid power products)
Parker acquires Aeroquip AC&R from Eaton
Parker acquires Sporlan Valve Co.
Parker acquires Virginia KMP
Parker acquires Microthermo Technologies
1940’s
Parker grows to 3 million in sales.
Parker Hannifin is first traded on the NYSE. Sales reach 200 M.
1964
1957
1970’s
Parker sales reach 500 million.
1980’s
Parker makes 36 acquisitions.
1990’s
Parker launches www.parker.com

## Slide 4: Parker Overview
Parker can be found on and around everything that moves.
Fluid Connectors
Instrumentation
Hydraulics
Automation
Filtration
Engineered Materials
Aerospace

## Slide 5: Parker – Sporlan Division
Filtration
Seal
Aerospace
Automation
Instrumentation
Hydraulics
Fluid Connectors
Sporlan
Washington, MO (3) New Haven, IN (1)
Greenfield, TN (1)
Owensville, MO (2)

## Slide 6: 13 SEER
More energy efficient motors (compressor and/or fans)
Variable Speed components
More surface area (larger equipment size)
Use of Thermostatic Expansion Valves
  Adds approx. ½ to 1 SEER

## Slide 7: Saturation Chart
What is the Temperature -Pressure Chart ? ?
P
T

## Slide 8: Temperature - Pressure Graph
-40 -20 0 20 40 60 80 100 120 140 160
Pressure (psig)
Temperature °F
100
200
300
400
500
700
600
Liquid
Gas
96°
14° Superheat
11° Subcool
110
85
Saturation
Subcooling
Heat removed from the refrigerant that causes its temperature to fall below its saturation point.
R-410A
Superheat
Heat added to the refrigerant vapor that causes its temperature to rise above its saturation point.

## Slide 9: TXV’s control superheat
Point of Complete
Vaporization
Saturated Refrigerant
Liquid Line
Superheated Suction
Vaporization

## Slide 10: Measuring Superheat
Actual temperature at bulb ……………... 57°F
Saturated temperature
corresponding to 143 psig ……………….. 50°F
Operating superheat …………………… 7°F
R-410A
143 psig
57
Notes: How do you determine superheat?
Determine suction pressure at the evaporator outlet with a gauge. On close coupled installations, suction pressure may be read at compressor suction connection.
Use pressure temperature chart to determine saturation temperature at observed suction pressure.
Measure suction gas temperature on the line at the expansion valve bulb's remote location.
Subtract saturation temperature (from Step 2) from suction gas temperature (from Step 3).
The difference is the superheat of the suction gas. (Example uses R-410A).

## Slide 11: Heat Transfer
Reduced use of Evaporator heat transfer surface
Maximum use of Evaporator heat transfer surface
Max safe use of Evaporator heat transfer surface
High Superheat
Normal Superheat
No Superheat

## Slide 12: System Performance
Outdoor Temperature °F
95°F
60°F
Evaporator Superheat
Flood
Capacity Rating Point
Fixed Restrictor
TXV
TXV Protects Compressor
TXV
Provides
Improved
Efficiency
120°F

## Slide 13: Thermostatic . . .
A Precision Metering Device …
Designed to regulate the flow of liquid refrigerant to an evaporator …
At a rate equal to the evaporation of the liquid in the evaporator …
By responding to the temperature of the vaporized refrigerant exiting the evaporator and the pressure in the evaporator.
A Thermostatic Expansion Valve is …

## Slide 14: Expansion Valve Anatomy
SENSING BULB
CAP TUBE
POWER ELEMENT
DIAPHRAGM
PAD
SPRING
SUPERHEAT ADJUSTMENT STEM
CAP
BODY
EXTERNAL EQUALIZER
INLET
OUTLET
O-RING SEAL
PISTON

## Slide 15: Balancing the Forces
Bulb Pressure (F1)
Valve driver (opening force)
Responds to refrigerant temperature changes exiting the evaporator
Evaporator Pressure (F2)
Represents the evaporator load on the system.
Determines the opening degree of the valve.
Spring Pressure (F3)
Constant.
Determines what superheat the valve operates at.
Must be physically changed to change the superheat.
The valve drives to a determined superheat with a specific opening degree and is dependent on the evaporator load.
F1 = F2 + F3

## Slide 16: Balance Port Construction
F3 = Superheat Spring Force.
  Closing Force
F3
F2 = Evaporator pressure.
  Closing Force
F2
F4 = High & Low side pressure differential times the port area.
  Opening force
F4
F1
F1 = Thermal Bulb pressure.
  Opening force
F4 Force is “Canceled” out in “balance ported” valves due to unique design of piston.
Notes: Balanced port valves respond to forces (F-1), (F-2) and (F-3) in a manner similar to conventional valves; however, they take a unique approach to the (F-4) force created by high and low side pressure differentials across the ball and valve orifice.
The area of the Parker Power Piston® is equal to the area of the port diameter. This force is cancelled out as the piston force and the force across the port are equal and opposite.
As inlet pressure changes, the (F-4) force changes but always remain equal and opposite and is cancelled out, therefore, variations in valve system pressures do not have any effect on the static superheat setting of the valve.

## Slide 17: Balanced Port Expansion Valve
R-410A
Evap. Outlet Temp = 57°F
Evap Saturation Temp = 50°F
Superheat = 7°F
F1 = F2 + F3
57°F
143 psig (F2)
50°F SST
162 psig
Spring (F3)
19 psig
F1 = 143 + 19
F1 = 162 psig

## Slide 18: Evaporator Load Increases
R-410A
Evap. Outlet Temp = 60°F
Evap Saturation Temp = 50°F
Superheat = 10°F
60°F
143 psig (F2)
50°F SST
170 psig
Spring (F3)
19 psig
F1 = F2 + F3
F1 = 143 + 19
F1 = 162 psig
Increase in Superheat causes the bulb pressure to increase. . causing the opening force to increase.
Increase in Load causes a temporary imbalance.

## Slide 19: Evaporator Load Decreases
R-410A
Evap. Outlet Temp = 55°F
Evap Saturation Temp = 50°F
Superheat = 5°F
55°F
143 psig (F2)
50°F SST
156 psig
Spring (F3)
19 psig
F1 = F2 + F3
F1 = 143 + 19
F1 = 162 psig
Decrease in Superheat causes the bulb pressure to decrease. . causing the valve to close.
Decrease in Load causes a temporary imbalance.

## Slide 20: Thermal Bulb Charge - Type
Universal Charge
MOP Ballast Charge
Large liquid charge
“Not Sensitive” to migration
Very small liquid charge
“Sensitive” to migration
Ballast brick – slows reaction
Cross Section

## Slide 21: MOP Operating Function
Pressure limiting charge feature that uses a small amount of charge to limit the TXV for protection.
Positive
  Keeps compressors within operating envelope.
  Prevents liquid floodback during certain start-up conditions.
Negative
  Charge migration
  Diaphragm and capillary tube must be warmer than bulb.

## Slide 22: MOP “Ballast” Function
Bulb temperature increase
Liquid surface heats quickly
Brick heated slowly
Gas re-condenses on brick surface
Bulb temperature decrease
Quick condensation on bulb inner surface
Condensation rate slows – part of brick remains warmer than surface
Slow opening
Fast closing

## Slide 23: Bulb Response
Bulb response to temperature change
MOP

## Slide 24: Operating Superheat Variation
Bulb response to temperature change
Anti-Hunt
Standard

## Slide 25: Select a Valve
Capacity
Refrigerant
Application

## Slide 26: Parker TXV’s
N Series ( 1/4 to 3 tons)
Low Profile coolers, Ice Machines, Beverage Dispensers
H(E) & HC(E) Series ( 3/4 to 5 tons)
Air Conditioning, Heat Pumps
Balanced Port
C(E) Series ( 1/8 to 6 tons)
Refrigeration, Supermarket, AC
Balanced Port
EC(E) Series ( 1/8 to 15 tons)
Refrigeration, Supermarket, AC
Balanced Port
SC(E) Series ( 1/8 to 6 tons)
Refrigeration, Supermarket, AC
Balanced Port
EBSE Series ( 8 to 20 tons)
AC, Chillers, Refrigeration
Balanced Port
OE Series ( 15 to 70 tons)
AC, Chillers, Refrigeration
Balanced Port

## Slide 27: Residential AC TXV Kit Air Conditioning and Heat Pump
Kit covers Residential AC & Heat Pumps from 1½ to 5 Tons
Four Sweat Connection Valves with Adjustable Superheat
Five Adapters (Aeroquip, Chatleff and Flare) *
Fits All OEM brands and replacement coils
Aero Style
Chatleff Style
3/8” SAE
* (Equipment Manufacturers use either Aeroquip, Chatleff, or direct TXV braze)
Refrigerant R-22, R-407C |  |  |  |  | 
Model No. | Part No. | Capacity (T) | Inlet | Outlet | Equalizer
HCAE-3-VX100 | 040727-01 | 1½ - 3 | ⅜” ODF | ½” ODF | ¼” FL. NUT
HCAE-5-VX100 | 040728-01 | 3½ - 5 | ⅜” ODF | ⅝” ODF | ¼” FL. NUT
Refrigerants R-410A |  |  |  |  | 
Model No. | Part No. | Capacity (T) | Inlet | Outlet | Equalizer
HCAE-3-ZX200 | 040771-01 | 1½ - 3 | ⅜” ODF | ½” ODF | ¼” FL. NUT
HCAE-5-ZX200 | 040772-01 | 3½ - 5 | ⅜” ODF | ⅝” ODF | ¼” FL. NUT
Outlet Connection Adapters |  |  |  |  | 
Model No. |  | Part No. | Model No. |  | Part No.
5/8” ODM x Aeroquip Fitting |  | 183372 | 1/2” ODM x Chatleff Fitting |  | 183375
1/2” ODM x Aeroquip Fitting |  | 183373 | 1/2” ODM x 3/8” SAE |  | 183376
5/8” ODM x Chatleff Fitting |  | 183374 |  |  | 

## Slide 28: Select a Power Element
Application | Evaporator Range (°F) | R-22 R-407C | R-12 R-134a | R-502 R-404A | R-410A
Low Temp Refrigeration | -40° to 0° | VZ | - | SZ | -
Commercial Refrigeration | -40° to +60° | VW | JW | SW | -
Low Temp Pres. Limit | -40° to 0° | VX35 | - | SX35 | -
Commercial Pres. Limit | -10° to +60° | VX100 | JX60 | SX110 | ZX200
Air Conditioning | +30° to +60° | VX100 | JX60 | SX110 | ZX200
Heat Pump | -15° to +60° | VX100 | - | - | ZX200
Refrigerant
Application

## Slide 29: TXV Installation Considerations
GOOD THERMAL CONTACT
Straight Clean Surface to mount the bulb and Clamp Tight.
NEVER mount on Coupling or Joint.
Avoid vertical pipe if possible.
Locate close to evaporator outlet.
FULLY INSULATE the Thermal Bulb.
Thermal Bulb Mounting
Notes: Bulb Location and Installation
Since the control response of the bulb is crucial for satisfactory operation, care should be taken in its mounting and positioning.
· Always make sure the suction line is cleaned before clamping the bulb in place.
· On lines that are 5/8 " O.D. or smaller, the bulb may be installed on top of the line or side mounted (preferably at the 3 o'clock position).
· On lines that are 1 " O.D. or larger, the remote bulb should be installed at 45° or at approximately the 4 or 8 o'clock position.
· Never mount a bulb on the bottom of suction lines because a mixture of refrigerant and oil may be present at that point, especially on smaller lines.
· It is good practice to insulate the bulb regardless of the refrigerant type. This ensures that the bulb will only respond to the suction gas temperature and will not be affected by condensation, ice formation or ambient temperatures.
· Avoid mounting the bulb on vertical lines or close to reversing valves.
· The bulb should always be mounted between the evaporator outlet and the external equalizer connection and should be as close to the evaporator outlet as possible (generally 3 to 6 inches).
· On systems that have multiple evaporators, the bulb must be mounted on the suction line of the evaporator that it controls. Do not mount the bulb on the common suction line.
· Install traps on vertical risers.

## Slide 30: TXV Installation Considerations
Thermal Bulb Location
Mount on top or sides for 7/8” or smaller
6
12
2
4
Do Not mount Bulb on bottom of Suction line.
Mount on sides just below center for 1” and larger
Bulb
Bulb
Bulb
Bulb
8
10
Notes: Bulb Location and Installation
Since the control response of the bulb is crucial for satisfactory operation, care should be taken in its mounting and positioning.
· Always make sure the suction line is cleaned before clamping the bulb in place.
· On lines that are 7/8 " O.D. or smaller, the bulb may be installed on top of the line or side mounted (preferably at the 3 o'clock position).
· On lines that are 1 " O.D. or larger, the remote bulb should be installed at 45° or at approximately the 4 or 8 o'clock position.
· Never mount a bulb on the bottom of suction lines because a mixture of refrigerant and oil may be present at that point, especially on smaller lines.
· It is good practice to insulate the bulb regardless of the refrigerant type. This ensures that the bulb will only respond to the suction gas temperature and will not be affected by condensation, ice formation or ambient temperatures.
· Avoid mounting the bulb on vertical lines or close to reversing valves.
· The bulb should always be mounted between the evaporator outlet and the external equalizer connection and should be as close to the evaporator outlet as possible (generally 3 to 6 inches).
· On systems that have multiple evaporators, the bulb must be mounted on the suction line of the evaporator that it controls. Do not mount the bulb on the common suction line.
· Install traps on vertical risers.

## Slide 31: Thermal Bulb
NOT a Proper Installation
Use the metal straps or clamp provided by the valve manufacturer.

## Slide 32: Thermal Bulb Clamps
An example of a metal clamp provided by the equipment manufacturer.
New Style of a metal clamp provided by Parker.

## Slide 33: External Equalizer
Some TXV’s have an external pressure equalization line installed in the suction line.
External equalized TXV’s are necessary for proper TXV function when evaporators have a large pressure drop (generally over 3 psi).
Notes: External Equalizer Use
Use external equalizers for evap / distributor pressure drops over 3 psi.
Can be mounted upstream or downstream of bulb for Parker valves due to balanced port construction - keep toward top of suction line to prevent oil logging.

## Slide 34: Equalizer Line
Installation issues
Frost on Equalizer Line
Equalizer Line - bottom

## Slide 35: TXV Installation Considerations
Brazing
Limit body temperature to 250°F to prevent internal seals damage.
  Do not disassemble valves for installation, WRAP VALVE BODY, or use a Thermal Block.
  Remove Thermal Bulb from suction line before brazing
Notes: Brazing
Limit body temperature to 250°F (120° C) due to internal seals used for balanced port construction.
Do not disassemble valves for installation (WRAP VALVE BODY)

## Slide 36: TXV Valve Orientation
Most valves are not position sensitive.
However, optimal operation is achieved with power element UP to avoid oil accumulation near diaphragm.
Notes: Valve Orientation
Parker valves are not position sensitive; however, optimal operation is achieved with power element UP to avoid oil accumulation near diaphragm cavity.

## Slide 37: TXV Superheat Adjustment
Counter-clockwise increases refrigerant flow thus decreasing superheat
Clockwise decreases refrigerant flow thus increasing superheat
View of Adjustment Stem
Clockwise - Higher SH
Counter-Clockwise Lower SH
  Must have Proper system refrigerant charge.
  Must have Proper Air Flow across coil.
  Must be AT or NEAR design operating conditions.
Notes: Superheat Adjustment
Superheat degrees / turn varies per refrigerant and evaporator temperature
Clockwise increases superheat / Decreases refrigerant flow
Counter clockwise decreases superheat / Increases refrigerant flow

## Slide 38: TXV Troubleshooting
Symptom
Look for . . .
High Operating Superheat
Low refrigerant charge.
  Insufficient Subcooling
Improperly adjusted TXV.
Excessive pressure drop w/ internally equalized TXV.
Contamination blocking valve.
TXV leaking bulb charge.

## Slide 39: TXV Troubleshooting
Low Operating Superheat
Poor bulb mounting / contact (bulb senses too high temp.)
Improperly adjusted TXV.
Contamination in valve not allowing it to close fully.
An oversized valve
Oil logging in the evaporator
Symptom
Look for . . .

## Slide 40: TXV Troubleshooting
Valve Hunting
Oversized expansion valve (valve overcompensates)
Thermal bulb too far from Evap. Outlet.
Incorrect type bulb charge (“X” charges have best stability)
Uneven heat loading in multi-circuit evaporator (flooding circuit(s) affects suction line temperature)
Poor distribution or unequal circuit loading (Oil logging?)
Symptom
Look for . . .

## Slide 41: Thank You
www.parker.com/coolparts
1-800-742-2681