## Slide 1
Level 2
INVERTER UNITARY TRAINING
Ecoer Heat Pump Operation and Service Presentation

## Slide 2
TABLE OF CONTENTS
Heat Pump Components Identification
Heating Cooling Flow Diagram
Defrost Flow Diagram
Key Product Components
Heat Pump Error Codes
Air Handler Installation
Low Voltage Controls
Gateway Installation
Final Notes

## Slide 3
Level 2
Ecoer Smart Service App
Download from the app store

## Slide 4
Tabs

## Slide 5
Systems

## Slide 6
ESI Gateway

## Slide 7
Log in www.ecoer.com or App >Files >Installation to get the latest user manual for Ecoer Smart Service (ESS) Pro App.
Gateway App Overview

## Slide 8
Gateway APP Installation

## Slide 9
Gateway App Installation

## Slide 10
IoT Device INSTALLATION
To keep the best LTE signal, choose one side that is further away from the wall to hook up the IoT device to the condensing unit. Use screw to tighten the device and tie wrap to secure the cable.
The 1st row of the grille
1-a
1-b
1-c
1-d

## Slide 11
IoT Device INSTALLATION
Wiring
Unscrew the cable locker cap and securely fasten the waterproof joint to the reserved hole (plug has to be removed).
2-a
2-b
Remove the reserved plug
2-c
2-d
Unscrew the locker cap

## Slide 12
IoT Device INSTALLATION
Wiring
Plug the male blue terminal into CN11 (IoT) connector on main control board of outdoor unit.

## Slide 13
Gateway Installation
Ecoer Smart Service (ESS) Pro App is a tool that dealers can use to maintain
and monitor an Ecoer AC / HP system.
This App will display operational data of each system installed and allow continuous monitoring. Dealers will receive system alerts and service messages in real time, allowing for remote diagnostics and faster, more accurate responses.
ESS Pro App has three main pages:
“Systems” includes MY LIST and DEMO. See more details about the interface in the following page.
“Events” provides real-time alerts for systems you have installed.
“Files” presents training videos and technical manuals (e.g. Product Data, Installation, Service and so on)

## Slide 14
Gateway Installation

## Slide 15
Gateway Installation

## Slide 16
Gateway Installation

## Slide 17
Gateway Registration

## Slide 18
Gateway Registration

## Slide 19
Gateway Registration
Sign an agreement with homeowner to start the registration.
Touch Privacy Statement in “Green color” and show it to the homeowner. Type in homeowner’s name, unit location and other required information. Ask the homeowner to sign his/her name for your monitoring request and ecoer system registration. (Ecoer uses independent cellular data to monitor the condensing unit only.)
If homeowner is not present your signature is acceptable

## Slide 20
Gateway Registration

## Slide 21
Register a new AC
Serial Number
Touch button to scan IoT SN.
ESS Pro App INSTALLATION

## Slide 22
Register a new AC
Four sides
Touch button to scan ODU SN.
ESS Pro App INSTALLATION

## Slide 23
Register a new AC
Remarks:
Indoor unit SN may not needed if Ecoer condensing units match with other brands IDU.
E Series Air Handler
Touch button to scan IDU SN.
ESS Pro App INSTALLATION

## Slide 24
Register a new AC
Two sides
Remarks:
Indoor unit SN may not needed if Ecoer condensing units match with other brands IDU.
Touch button to scan IDU SN.
G Series
Cased Coil
ESS Pro App INSTALLATION

## Slide 25
Technical Manuals
Technical documents can be browsed on ESS Pro App.
Ecoer certified Distributors / Dealers are able to download original files at www.ecoer.com after your login.
ESS Pro App INSTALLATION

## Slide 26
Function and Control
ODU Functional Parts Layout
DC Motor (FAN)
Main Control Board (PCB)
Accumulator (ACC)
Noise Filter
Inductance
Fan Blades
Heat Exchanger
Liquid/Gas Service Valve
Inverter Compressor (INV)
Reversing Valve (ST1)
Electronic Expansion Valve (EEV)
Strainers
Gauge Port
High Pressure Sensor (HP) Black
Low Pressure Sensor (LP) Green
Lower Side Plate
Key Product Components

## Slide 27
Function and Control
HP
TD
EEV
INV Compressor
TH
TA
ST1
TS
TL
ACC
Liquid Service Valve
Heat Exchanger
Gas Service Valve
Gauge Port
FAN
LP
ODU Refrigerant circuit diagrams

## Slide 28
Function and Control
HP
TD
EEV
INV
TH
TA
ST1
TS
TL
ACC
Liquid Service Valve
Heat Exchanger
Gas Service Valve
Gauge Port
FAN
LP
ODU Refrigerant circuit diagrams
Name | Symbol | Function
Inverter compressor | INV | Adjusts refrigerant flow rate by changing the compressor speed (RPS) based on objective pressure.
DC motor | FAN | Outputs heat exchanger capacity by adjusting the motor rotation speed based on operating pressure.
Electronic expansion valve | EEV | Fully open during cooling mode and defrostoperation. Control compressor discharge superheat in heatingmode.
Reversing valve | ST1 | Switches the operation mode between heating and cooling (including defrost control).
Temperature sensor | TH | Uses to control defrosting during heating operation.
 | TA | Uses to detect outdoor air temperature and control fan speed.
 | TS | Uses to detect compressor suction temperature and calculate compressor suction superheat (SH).
 | TL | Uses to detect liquid line temperature and calculate sub-cooling (SC).
 | TD | Uses to detect compressor discharge temperature and calculate compressor discharge superheat (DSH).
 | TF | Uses to detect heat sink temperature of inverter module.
High pressure sensor | HP | Uses to detect high pressure.
Low pressure sensor | LP | Uses to detect low pressure.
Accumulator | ACC | Uses to store excess refrigerant.

## Slide 29
Heat Pump Component Identification and Test
ACC
ODU Refrigerant circuit diagrams

## Slide 30
Function and Control
Main Circuit Board Pin-out Diagrams 2436

## Slide 31
Function and Control
Main Circuit Board Pin-out Diagrams 4860

## Slide 32
Function and Control
Operation Mode
After 1 minute
Thermostat ON (Y=ON)
Thermostat OFF (Y=OFF)
O signal change
MAX. 6 minutes
Malfunction
Cooling or heating operation
Normal operation
Compressor PI control
EEV PI control
Fan motor control
Protection control
Oil return IN conditions are met.
NO
YES
Oil return operation *NOTE
Defrost IN conditions are met.
YES
NO
Pressure equalizing prior to start-up
Restart standby (compressor stops)
Start-up control *NOTE
・Cooling start-up (O=ON)
・Heating start-up (O=OFF)
Defrost operation *NOTE
Operation in stop mode

## Slide 33
Function and Control
Operation Mode
Input Signal | Actuator | Cooling control (including cooling oil return) | Heating control (including heating oil return)
Y | Compressor (INV) | Apply Compressor PI control to maintain Tes*1 | Apply Compressor PI control to maintain Tcs*1
Y / O*2 | Outdoor fan (FAN) | Cooling fan control | Heating fan control
O*2 | Reversing valve (ST1) | Energized 208/230 VAC | De-energized
Y / O*2 | Electronic expansion valve (EEV) | 480pls | PI control to maintain discharge superheat (DSH)
Tes: Target Te value (Varies depending on the load of space, mode choice, silent setting)
Te: Low pressure equivalent saturation temperature (°F)
Tcs: Target Tc value (Varies depending on the load of space, mode choice, silent setting)
Tc: High pressure equivalent saturation temperature (°F)

## Slide 34
Function and Control
Defrost Control
This system carries out demand defrost control if any one of the following conditions satisfy.
The calculated temperature difference between ambient temperature (TA) and outdoor coil temperature (TH) is called Delta T. After Delta T is achieved and continues for 5 minutes.
41°F < TA < 59°F, TH ≤ 30°F, Delta T = 18°F
b) 19°F ≤ TA ≤ 41°F, TH ≤ 30°F, Delta T = 12~18°F
c) TA <19°F, TH < 9°F,
Accumulative compressor run time ≥ 80 minutes
Coil Temperature (TH) backup running, TA < 59°F and LP ≤ 90psi,+ accumulative compressor run time ≥ 60 minutes
After “Minimum Run Time” (MRT) is achieved.
  MRT is 3.5 hours when TA <23°F
  MRT is 2 hours when 23°F ≤ TA < 43°F
Defrost will be terminated once outdoor coil temperature sensor (TH) reaches 64°F for 60 seconds or the defrost time has exceeded 8 minutes. Defrost mode setting (n04) offers termination options for different geographical conditions.
  Defrost in heavy snow area will extend defrost for 60 seconds, but reduce the heating time to execute more defrost operations.
b) Defrost in light snow area will reduce defrost for 30seconds.

## Slide 35
Function and Control
Defrost Control
This system carries out demand defrost control if any one of the following conditions satisfy.
The high pressure drops below 245psi for 20 minutes when 14°F ≤ TA ≤ 28°F.
Manual defrosting can be chosen from n08 setting.
Start-up control is enforced to complete, then wait another 5 minutes to activate the defrost operation.
Defrost will be terminated once defrost temperature sensor (TH) reaches 64°F for 60 seconds or the defrost time has exceeded 8 minutes. Defrost mode setting (n04) offers termination options for different geographical conditions.
  Defrost in heavy snow area will extend defrost for 60 seconds, but reduce the heating time to execute more defrost operations.
b) Defrost in light snow area will reduce defrost for 30seconds.

## Slide 36
Function and Control
Test (Auto Charge) Control
Input Signal | Actuator | Cooling control (including cooling oil return) | Heating control (including heating oil return)
Y | Compressor (INV) | 2ton: 56rps→26rps 3ton: 66rps→36rps 4ton: 56rps→26rps 5ton: 66rps→36rps | 2ton: 66rps→26rps 3ton: 80rps→36rps 4ton: 58rps→26rps 5ton: 70rps→36rps
Y / O*2 | Outdoor fan (FAN) | Cooling fan control | Heating fan control
O*2 | Reversing valve (ST1) | Energized 208/230 VAC When energized, the Reversing Valve is de-energized | De-energized 208/230 VAC When de-energized, the Reversing Valve is energized
Y / O*2 | Electronic expansion valve (EEV) | 480pls | PI control to maintain discharge superheat (DSH)

## Slide 37
13/30
ESI Unitary System Troubleshooting
Sensors and Faults

## Slide 38
13/30
ESI Unitary System Troubleshooting
Display
Ambient temperature sensor fault (TA）
Error definition:
The outside temperature sensor (TA) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged temperature sensor
There are other heat sources around the sensor
YES
NO
Check whether TA sensor is seated to the specified location and connected to CN2 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the faulty sensor
Are there any other heat sources around the sensor?
NO
YES
Remove other heat source
Can the system go into backup running?
YES
Replace the sensor
Replace the main control board
NO

## Slide 39
Board Location CN2
Ambient Temperature Sensor
Ambient Temperature Sensor 10k Thermistor
Temp. (°C) | Temp. (°F) | Resistanc e (KΩ) | Voltage (V)
-20 | -4 | 104.86 | 0.53
-19 | -2.2 | 98.84 | 0.56
-18 | -0.4 | 93.21 | 0.58
-17 | 1.4 | 87.93 | 0.61
-16 | 3.2 | 82.98 | 0.64
-15 | 5 | 78.33 | 0.67
-14 | 6.8 | 73.97 | 0.70
-13 | 8.6 | 69.88 | 0.73
-12 | 10.4 | 66.03 | 0.77
-11 | 12.2 | 62.42 | 0.80
-10 | 14 | 59.02 | 0.84
-9 | 15.8 | 55.82 | 0.87
-8 | 17.6 | 52.81 | 0.91
-7 | 19.4 | 49.98 | 0.94
-6 | 21.2 | 47.32 | 0.98
-5 | 23 | 44.81 | 1.02
-4 | 24.8 | 42.45 | 1.06
-3 | 26.6 | 40.22 | 1.10
-2 | 28.4 | 38.12 | 1.14
-1 | 30.2 | 36.15 | 1.18
0 | 32 | 34.28 | 1.22
1 | 33.8 | 32.52 | 1.26
2 | 35.6 | 30.86 | 1.30
3 | 37.4 | 29.29 | 1.34
4 | 39.2 | 27.81 | 1.38
5 | 41 | 26.42 | 1.42
6 | 42.8 | 25.10 | 1.46
7 | 44.6 | 23.85 | 1.51
8 | 46.4 | 22.67 | 1.55
9 | 48.2 | 21.56 | 1.59
10 | 50 | 20.50 | 1.63
11 | 51.8 | 19.51 | 1.67
12 | 53.6 | 18.56 | 1.71
13 | 55.4 | 17.67 | 1.75
14 | 57.2 | 16.83 | 1.79
15 | 59 | 16.03 | 1.83
16 | 60.8 | 15.27 | 1.87
17 | 62.6 | 14.55 | 1.91
18 | 64.4 | 13.87 | 1.95
19 | 66.2 | 13.23 | 1.99
20 | 68 | 12.62 | 2.02
21 | 69.8 | 12.04 | 2.06
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
22 | 71.6 | 11.49 | 2.10
23 | 73.4 | 10.97 | 2.13
24 | 75.2 | 10.47 | 2.17
25 | 77 | 10.00 | 2.20
26 | 78.8 | 9.55 | 2.23
27 | 80.6 | 9.13 | 2.27
28 | 82.4 | 8.73 | 2.30
29 | 84.2 | 8.35 | 2.33
30 | 86 | 7.98 | 2.36
31 | 87.8 | 7.64 | 2.39
32 | 89.6 | 7.31 | 2.42
33 | 91.4 | 6.99 | 2.44
34 | 93.2 | 6.70 | 2.47
35 | 95 | 6.41 | 2.50
36 | 96.8 | 6.14 | 2.52
37 | 98.6 | 5.89 | 2.55
38 | 100.4 | 5.64 | 2.57
39 | 102.2 | 5.41 | 2.60
40 | 104 | 5.19 | 2.62
41 | 105.8 | 4.97 | 2.64
42 | 107.6 | 4.77 | 2.66
43 | 109.4 | 4.58 | 2.69
44 | 111.2 | 4.39 | 2.71
45 | 113 | 4.22 | 2.73
46 | 114.8 | 4.05 | 2.74
47 | 116.6 | 3.89 | 2.76
48 | 118.4 | 3.74 | 2.78
49 | 120.2 | 3.59 | 2.80
50 | 122 | 3.45 | 2.81
51 | 123.8 | 3.32 | 2.83
52 | 125.6 | 3.19 | 2.85
53 | 127.4 | 3.07 | 2.86
54 | 129.2 | 2.95 | 2.88
55 | 131 | 2.84 | 2.89
56 | 132.8 | 2.73 | 2.90
57 | 134.6 | 2.63 | 2.92
58 | 136.4 | 2.53 | 2.93
59 | 138.2 | 2.44 | 2.94
60 | 140 | 2.35 | 2.95
61 | 141.8 | 2.26 | 2.96
62 | 143.6 | 2.18 | 2.98
63 | 145.4 | 2.10 | 2.99
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
64 | 147.2 | 2.02 | 3.00
65 | 149 | 1.95 | 3.01
66 | 150.8 | 1.88 | 3.02
67 | 152.6 | 1.81 | 3.03
68 | 154.4 | 1.75 | 3.04
69 | 156.2 | 1.68 | 3.04
70 | 158 | 1.63 | 3.05
71 | 159.8 | 1.57 | 3.06
72 | 161.6 | 1.51 | 3.07
73 | 163.4 | 1.46 | 3.08
74 | 165.2 | 1.41 | 3.08
75 | 167 | 1.36 | 3.09
76 | 168.8 | 1.31 | 3.10
77 | 170.6 | 1.27 | 3.10
78 | 172.4 | 1.23 | 3.11
79 | 174.2 | 1.19 | 3.12
80 | 176 | 1.15 | 3.12
81 | 177.8 | 1.11 | 3.13
82 | 179.6 | 1.07 | 3.13
83 | 181.4 | 1.03 | 3.14
84 | 183.2 | 1.00 | 3.14
85 | 185 | 0.97 | 3.15
86 | 186.8 | 0.94 | 3.15
87 | 188.6 | 0.91 | 3.16
88 | 190.4 | 0.88 | 3.16
89 | 192.2 | 0.85 | 3.17
90 | 194 | 0.82 | 3.17
91 | 195.8 | 0.80 | 3.17
92 | 197.6 | 0.77 | 3.18
93 | 199.4 | 0.75 | 3.18
94 | 201.2 | 0.72 | 3.18
95 | 203 | 0.70 | 3.19
96 | 204.8 | 0.68 | 3.19
97 | 206.6 | 0.66 | 3.19
98 | 208.4 | 0.64 | 3.20
99 | 210.2 | 0.62 | 3.20
100 | 212 | 0.60 | 3.20
101 | 213.8 | 0.59 | 3.21
102 | 215.6 | 0.57 | 3.21
103 | 217.4 | 0.55 | 3.21
104 | 219.2 | 0.54 | 3.21
105 | 221 | 0.52 | 3.22

## Slide 40
14/30
ESI Unitary System Troubleshooting
Display
YES
NO
Check whether TS sensor is seated to the suction pipe and connected to CN2 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the faulty sensor
Are there any other heat sources around the sensor?
NO
YES
Remove other heat source
Can the system go into backup running?
YES
Replace the sensor
Replace the main control board
NO
Suction temperature sensor fault (TS)
Error definition:
The suction temperature sensor (TS) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged temperature sensor
There are other heat sources around the sensor

## Slide 41
Board Location CN2
Suction Temperature Sensor
Temp. (°C) | Temp. (°F) | Resistanc e (KΩ) | Voltage (V)
-20 | -4 | 104.86 | 0.53
-19 | -2.2 | 98.84 | 0.56
-18 | -0.4 | 93.21 | 0.58
-17 | 1.4 | 87.93 | 0.61
-16 | 3.2 | 82.98 | 0.64
-15 | 5 | 78.33 | 0.67
-14 | 6.8 | 73.97 | 0.70
-13 | 8.6 | 69.88 | 0.73
-12 | 10.4 | 66.03 | 0.77
-11 | 12.2 | 62.42 | 0.80
-10 | 14 | 59.02 | 0.84
-9 | 15.8 | 55.82 | 0.87
-8 | 17.6 | 52.81 | 0.91
-7 | 19.4 | 49.98 | 0.94
-6 | 21.2 | 47.32 | 0.98
-5 | 23 | 44.81 | 1.02
-4 | 24.8 | 42.45 | 1.06
-3 | 26.6 | 40.22 | 1.10
-2 | 28.4 | 38.12 | 1.14
-1 | 30.2 | 36.15 | 1.18
0 | 32 | 34.28 | 1.22
1 | 33.8 | 32.52 | 1.26
2 | 35.6 | 30.86 | 1.30
3 | 37.4 | 29.29 | 1.34
4 | 39.2 | 27.81 | 1.38
5 | 41 | 26.42 | 1.42
6 | 42.8 | 25.10 | 1.46
7 | 44.6 | 23.85 | 1.51
8 | 46.4 | 22.67 | 1.55
9 | 48.2 | 21.56 | 1.59
10 | 50 | 20.50 | 1.63
11 | 51.8 | 19.51 | 1.67
12 | 53.6 | 18.56 | 1.71
13 | 55.4 | 17.67 | 1.75
14 | 57.2 | 16.83 | 1.79
15 | 59 | 16.03 | 1.83
16 | 60.8 | 15.27 | 1.87
17 | 62.6 | 14.55 | 1.91
18 | 64.4 | 13.87 | 1.95
19 | 66.2 | 13.23 | 1.99
20 | 68 | 12.62 | 2.02
21 | 69.8 | 12.04 | 2.06
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
22 | 71.6 | 11.49 | 2.10
23 | 73.4 | 10.97 | 2.13
24 | 75.2 | 10.47 | 2.17
25 | 77 | 10.00 | 2.20
26 | 78.8 | 9.55 | 2.23
27 | 80.6 | 9.13 | 2.27
28 | 82.4 | 8.73 | 2.30
29 | 84.2 | 8.35 | 2.33
30 | 86 | 7.98 | 2.36
31 | 87.8 | 7.64 | 2.39
32 | 89.6 | 7.31 | 2.42
33 | 91.4 | 6.99 | 2.44
34 | 93.2 | 6.70 | 2.47
35 | 95 | 6.41 | 2.50
36 | 96.8 | 6.14 | 2.52
37 | 98.6 | 5.89 | 2.55
38 | 100.4 | 5.64 | 2.57
39 | 102.2 | 5.41 | 2.60
40 | 104 | 5.19 | 2.62
41 | 105.8 | 4.97 | 2.64
42 | 107.6 | 4.77 | 2.66
43 | 109.4 | 4.58 | 2.69
44 | 111.2 | 4.39 | 2.71
45 | 113 | 4.22 | 2.73
46 | 114.8 | 4.05 | 2.74
47 | 116.6 | 3.89 | 2.76
48 | 118.4 | 3.74 | 2.78
49 | 120.2 | 3.59 | 2.80
50 | 122 | 3.45 | 2.81
51 | 123.8 | 3.32 | 2.83
52 | 125.6 | 3.19 | 2.85
53 | 127.4 | 3.07 | 2.86
54 | 129.2 | 2.95 | 2.88
55 | 131 | 2.84 | 2.89
56 | 132.8 | 2.73 | 2.90
57 | 134.6 | 2.63 | 2.92
58 | 136.4 | 2.53 | 2.93
59 | 138.2 | 2.44 | 2.94
60 | 140 | 2.35 | 2.95
61 | 141.8 | 2.26 | 2.96
62 | 143.6 | 2.18 | 2.98
63 | 145.4 | 2.10 | 2.99
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
64 | 147.2 | 2.02 | 3.00
65 | 149 | 1.95 | 3.01
66 | 150.8 | 1.88 | 3.02
67 | 152.6 | 1.81 | 3.03
68 | 154.4 | 1.75 | 3.04
69 | 156.2 | 1.68 | 3.04
70 | 158 | 1.63 | 3.05
71 | 159.8 | 1.57 | 3.06
72 | 161.6 | 1.51 | 3.07
73 | 163.4 | 1.46 | 3.08
74 | 165.2 | 1.41 | 3.08
75 | 167 | 1.36 | 3.09
76 | 168.8 | 1.31 | 3.10
77 | 170.6 | 1.27 | 3.10
78 | 172.4 | 1.23 | 3.11
79 | 174.2 | 1.19 | 3.12
80 | 176 | 1.15 | 3.12
81 | 177.8 | 1.11 | 3.13
82 | 179.6 | 1.07 | 3.13
83 | 181.4 | 1.03 | 3.14
84 | 183.2 | 1.00 | 3.14
85 | 185 | 0.97 | 3.15
86 | 186.8 | 0.94 | 3.15
87 | 188.6 | 0.91 | 3.16
88 | 190.4 | 0.88 | 3.16
89 | 192.2 | 0.85 | 3.17
90 | 194 | 0.82 | 3.17
91 | 195.8 | 0.80 | 3.17
92 | 197.6 | 0.77 | 3.18
93 | 199.4 | 0.75 | 3.18
94 | 201.2 | 0.72 | 3.18
95 | 203 | 0.70 | 3.19
96 | 204.8 | 0.68 | 3.19
97 | 206.6 | 0.66 | 3.19
98 | 208.4 | 0.64 | 3.20
99 | 210.2 | 0.62 | 3.20
100 | 212 | 0.60 | 3.20
101 | 213.8 | 0.59 | 3.21
102 | 215.6 | 0.57 | 3.21
103 | 217.4 | 0.55 | 3.21
104 | 219.2 | 0.54 | 3.21
105 | 221 | 0.52 | 3.22
(TS) Suction Temperature Sensor 10k Thermistor

## Slide 42
15/30
ESI Unitary System Troubleshooting
Display
Liquid temperature sensor fault (TL)
Error definition:
The liquid temperature sensor (TL) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged temperature sensor
There are other heat sources around the sensor
YES
NO
Check whether TL sensor is seated to the specified location and connected to CN4 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the faulty sensor
Are there any other heat sources around the sensor?
NO
YES
Remove other heat source
Can the system go into backup running?
YES
Replace the sensor
Replace the main control board
NO

## Slide 43
Board Location CN4
Liquid Temperature Sensor
(TL) Liquid Line Temperature Sensor 10k Thermistor
Temp. (°C) | Temp. (°F) | Resistanc e (KΩ) | Voltage (V)
-20 | -4 | 104.86 | 0.53
-19 | -2.2 | 98.84 | 0.56
-18 | -0.4 | 93.21 | 0.58
-17 | 1.4 | 87.93 | 0.61
-16 | 3.2 | 82.98 | 0.64
-15 | 5 | 78.33 | 0.67
-14 | 6.8 | 73.97 | 0.70
-13 | 8.6 | 69.88 | 0.73
-12 | 10.4 | 66.03 | 0.77
-11 | 12.2 | 62.42 | 0.80
-10 | 14 | 59.02 | 0.84
-9 | 15.8 | 55.82 | 0.87
-8 | 17.6 | 52.81 | 0.91
-7 | 19.4 | 49.98 | 0.94
-6 | 21.2 | 47.32 | 0.98
-5 | 23 | 44.81 | 1.02
-4 | 24.8 | 42.45 | 1.06
-3 | 26.6 | 40.22 | 1.10
-2 | 28.4 | 38.12 | 1.14
-1 | 30.2 | 36.15 | 1.18
0 | 32 | 34.28 | 1.22
1 | 33.8 | 32.52 | 1.26
2 | 35.6 | 30.86 | 1.30
3 | 37.4 | 29.29 | 1.34
4 | 39.2 | 27.81 | 1.38
5 | 41 | 26.42 | 1.42
6 | 42.8 | 25.10 | 1.46
7 | 44.6 | 23.85 | 1.51
8 | 46.4 | 22.67 | 1.55
9 | 48.2 | 21.56 | 1.59
10 | 50 | 20.50 | 1.63
11 | 51.8 | 19.51 | 1.67
12 | 53.6 | 18.56 | 1.71
13 | 55.4 | 17.67 | 1.75
14 | 57.2 | 16.83 | 1.79
15 | 59 | 16.03 | 1.83
16 | 60.8 | 15.27 | 1.87
17 | 62.6 | 14.55 | 1.91
18 | 64.4 | 13.87 | 1.95
19 | 66.2 | 13.23 | 1.99
20 | 68 | 12.62 | 2.02
21 | 69.8 | 12.04 | 2.06
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
22 | 71.6 | 11.49 | 2.10
23 | 73.4 | 10.97 | 2.13
24 | 75.2 | 10.47 | 2.17
25 | 77 | 10.00 | 2.20
26 | 78.8 | 9.55 | 2.23
27 | 80.6 | 9.13 | 2.27
28 | 82.4 | 8.73 | 2.30
29 | 84.2 | 8.35 | 2.33
30 | 86 | 7.98 | 2.36
31 | 87.8 | 7.64 | 2.39
32 | 89.6 | 7.31 | 2.42
33 | 91.4 | 6.99 | 2.44
34 | 93.2 | 6.70 | 2.47
35 | 95 | 6.41 | 2.50
36 | 96.8 | 6.14 | 2.52
37 | 98.6 | 5.89 | 2.55
38 | 100.4 | 5.64 | 2.57
39 | 102.2 | 5.41 | 2.60
40 | 104 | 5.19 | 2.62
41 | 105.8 | 4.97 | 2.64
42 | 107.6 | 4.77 | 2.66
43 | 109.4 | 4.58 | 2.69
44 | 111.2 | 4.39 | 2.71
45 | 113 | 4.22 | 2.73
46 | 114.8 | 4.05 | 2.74
47 | 116.6 | 3.89 | 2.76
48 | 118.4 | 3.74 | 2.78
49 | 120.2 | 3.59 | 2.80
50 | 122 | 3.45 | 2.81
51 | 123.8 | 3.32 | 2.83
52 | 125.6 | 3.19 | 2.85
53 | 127.4 | 3.07 | 2.86
54 | 129.2 | 2.95 | 2.88
55 | 131 | 2.84 | 2.89
56 | 132.8 | 2.73 | 2.90
57 | 134.6 | 2.63 | 2.92
58 | 136.4 | 2.53 | 2.93
59 | 138.2 | 2.44 | 2.94
60 | 140 | 2.35 | 2.95
61 | 141.8 | 2.26 | 2.96
62 | 143.6 | 2.18 | 2.98
63 | 145.4 | 2.10 | 2.99
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
64 | 147.2 | 2.02 | 3.00
65 | 149 | 1.95 | 3.01
66 | 150.8 | 1.88 | 3.02
67 | 152.6 | 1.81 | 3.03
68 | 154.4 | 1.75 | 3.04
69 | 156.2 | 1.68 | 3.04
70 | 158 | 1.63 | 3.05
71 | 159.8 | 1.57 | 3.06
72 | 161.6 | 1.51 | 3.07
73 | 163.4 | 1.46 | 3.08
74 | 165.2 | 1.41 | 3.08
75 | 167 | 1.36 | 3.09
76 | 168.8 | 1.31 | 3.10
77 | 170.6 | 1.27 | 3.10
78 | 172.4 | 1.23 | 3.11
79 | 174.2 | 1.19 | 3.12
80 | 176 | 1.15 | 3.12
81 | 177.8 | 1.11 | 3.13
82 | 179.6 | 1.07 | 3.13
83 | 181.4 | 1.03 | 3.14
84 | 183.2 | 1.00 | 3.14
85 | 185 | 0.97 | 3.15
86 | 186.8 | 0.94 | 3.15
87 | 188.6 | 0.91 | 3.16
88 | 190.4 | 0.88 | 3.16
89 | 192.2 | 0.85 | 3.17
90 | 194 | 0.82 | 3.17
91 | 195.8 | 0.80 | 3.17
92 | 197.6 | 0.77 | 3.18
93 | 199.4 | 0.75 | 3.18
94 | 201.2 | 0.72 | 3.18
95 | 203 | 0.70 | 3.19
96 | 204.8 | 0.68 | 3.19
97 | 206.6 | 0.66 | 3.19
98 | 208.4 | 0.64 | 3.20
99 | 210.2 | 0.62 | 3.20
100 | 212 | 0.60 | 3.20
101 | 213.8 | 0.59 | 3.21
102 | 215.6 | 0.57 | 3.21
103 | 217.4 | 0.55 | 3.21
104 | 219.2 | 0.54 | 3.21
105 | 221 | 0.52 | 3.22

## Slide 44
16/30
ESI Unitary System Troubleshooting
Display
Condenser coil temperature sensor fault (TH)
Error definition:
The condenser coil temperature sensor (TH) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged temperature sensor
There are other heat sources around the sensor
YES
NO
Check whether TH sensor is seated to the specified location and connected to CN4 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the faulty sensor
Are there any other heat sources around the sensor?
NO
YES
Remove other heat source
Can the system go into backup running?
YES
Replace the sensor
Replace the main control board
NO

## Slide 45
Board Location CN4
Condenser Temperature Sensor (Defrost Sensor)
Temp. (°C) | Temp. (°F) | Resistanc e (KΩ) | Voltage (V)
-20 | -4 | 104.86 | 0.53
-19 | -2.2 | 98.84 | 0.56
-18 | -0.4 | 93.21 | 0.58
-17 | 1.4 | 87.93 | 0.61
-16 | 3.2 | 82.98 | 0.64
-15 | 5 | 78.33 | 0.67
-14 | 6.8 | 73.97 | 0.70
-13 | 8.6 | 69.88 | 0.73
-12 | 10.4 | 66.03 | 0.77
-11 | 12.2 | 62.42 | 0.80
-10 | 14 | 59.02 | 0.84
-9 | 15.8 | 55.82 | 0.87
-8 | 17.6 | 52.81 | 0.91
-7 | 19.4 | 49.98 | 0.94
-6 | 21.2 | 47.32 | 0.98
-5 | 23 | 44.81 | 1.02
-4 | 24.8 | 42.45 | 1.06
-3 | 26.6 | 40.22 | 1.10
-2 | 28.4 | 38.12 | 1.14
-1 | 30.2 | 36.15 | 1.18
0 | 32 | 34.28 | 1.22
1 | 33.8 | 32.52 | 1.26
2 | 35.6 | 30.86 | 1.30
3 | 37.4 | 29.29 | 1.34
4 | 39.2 | 27.81 | 1.38
5 | 41 | 26.42 | 1.42
6 | 42.8 | 25.10 | 1.46
7 | 44.6 | 23.85 | 1.51
8 | 46.4 | 22.67 | 1.55
9 | 48.2 | 21.56 | 1.59
10 | 50 | 20.50 | 1.63
11 | 51.8 | 19.51 | 1.67
12 | 53.6 | 18.56 | 1.71
13 | 55.4 | 17.67 | 1.75
14 | 57.2 | 16.83 | 1.79
15 | 59 | 16.03 | 1.83
16 | 60.8 | 15.27 | 1.87
17 | 62.6 | 14.55 | 1.91
18 | 64.4 | 13.87 | 1.95
19 | 66.2 | 13.23 | 1.99
20 | 68 | 12.62 | 2.02
21 | 69.8 | 12.04 | 2.06
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
22 | 71.6 | 11.49 | 2.10
23 | 73.4 | 10.97 | 2.13
24 | 75.2 | 10.47 | 2.17
25 | 77 | 10.00 | 2.20
26 | 78.8 | 9.55 | 2.23
27 | 80.6 | 9.13 | 2.27
28 | 82.4 | 8.73 | 2.30
29 | 84.2 | 8.35 | 2.33
30 | 86 | 7.98 | 2.36
31 | 87.8 | 7.64 | 2.39
32 | 89.6 | 7.31 | 2.42
33 | 91.4 | 6.99 | 2.44
34 | 93.2 | 6.70 | 2.47
35 | 95 | 6.41 | 2.50
36 | 96.8 | 6.14 | 2.52
37 | 98.6 | 5.89 | 2.55
38 | 100.4 | 5.64 | 2.57
39 | 102.2 | 5.41 | 2.60
40 | 104 | 5.19 | 2.62
41 | 105.8 | 4.97 | 2.64
42 | 107.6 | 4.77 | 2.66
43 | 109.4 | 4.58 | 2.69
44 | 111.2 | 4.39 | 2.71
45 | 113 | 4.22 | 2.73
46 | 114.8 | 4.05 | 2.74
47 | 116.6 | 3.89 | 2.76
48 | 118.4 | 3.74 | 2.78
49 | 120.2 | 3.59 | 2.80
50 | 122 | 3.45 | 2.81
51 | 123.8 | 3.32 | 2.83
52 | 125.6 | 3.19 | 2.85
53 | 127.4 | 3.07 | 2.86
54 | 129.2 | 2.95 | 2.88
55 | 131 | 2.84 | 2.89
56 | 132.8 | 2.73 | 2.90
57 | 134.6 | 2.63 | 2.92
58 | 136.4 | 2.53 | 2.93
59 | 138.2 | 2.44 | 2.94
60 | 140 | 2.35 | 2.95
61 | 141.8 | 2.26 | 2.96
62 | 143.6 | 2.18 | 2.98
63 | 145.4 | 2.10 | 2.99
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
64 | 147.2 | 2.02 | 3.00
65 | 149 | 1.95 | 3.01
66 | 150.8 | 1.88 | 3.02
67 | 152.6 | 1.81 | 3.03
68 | 154.4 | 1.75 | 3.04
69 | 156.2 | 1.68 | 3.04
70 | 158 | 1.63 | 3.05
71 | 159.8 | 1.57 | 3.06
72 | 161.6 | 1.51 | 3.07
73 | 163.4 | 1.46 | 3.08
74 | 165.2 | 1.41 | 3.08
75 | 167 | 1.36 | 3.09
76 | 168.8 | 1.31 | 3.10
77 | 170.6 | 1.27 | 3.10
78 | 172.4 | 1.23 | 3.11
79 | 174.2 | 1.19 | 3.12
80 | 176 | 1.15 | 3.12
81 | 177.8 | 1.11 | 3.13
82 | 179.6 | 1.07 | 3.13
83 | 181.4 | 1.03 | 3.14
84 | 183.2 | 1.00 | 3.14
85 | 185 | 0.97 | 3.15
86 | 186.8 | 0.94 | 3.15
87 | 188.6 | 0.91 | 3.16
88 | 190.4 | 0.88 | 3.16
89 | 192.2 | 0.85 | 3.17
90 | 194 | 0.82 | 3.17
91 | 195.8 | 0.80 | 3.17
92 | 197.6 | 0.77 | 3.18
93 | 199.4 | 0.75 | 3.18
94 | 201.2 | 0.72 | 3.18
95 | 203 | 0.70 | 3.19
96 | 204.8 | 0.68 | 3.19
97 | 206.6 | 0.66 | 3.19
98 | 208.4 | 0.64 | 3.20
99 | 210.2 | 0.62 | 3.20
100 | 212 | 0.60 | 3.20
101 | 213.8 | 0.59 | 3.21
102 | 215.6 | 0.57 | 3.21
103 | 217.4 | 0.55 | 3.21
104 | 219.2 | 0.54 | 3.21
105 | 221 | 0.52 | 3.22
(TH) Condenser Temperature Sensor 10k Thermistor

## Slide 46
17/30
ESI Unitary System Troubleshooting
Display
Discharge temperature sensor fault (TD)
Error definition:
The discharge temperature sensor(TD) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Temperature sensor failure
There are other heat sources around the sensor
YES
NO
Check whether TD sensor is seated to the specified location and connected to CN7 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor B*.
YES
NO
Replace the faulty sensor
Check whether there are other heat sources around sensor
NO
YES
Remove all the other heat source
Can the system go into backup running?
YES
Replace the sensor
Replace the main control board
NO

## Slide 47
Board Location CN7
Discharge Temperature Sensor
(TD) Discharge Temperature Sensor
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
-20 | -4 | 517.84 | 0.27
-19 | -2.2 | 489.93 | 0.29
-18 | -0.4 | 463.65 | 0.30
-17 | 1.4 | 438.89 | 0.32
-16 | 3.2 | 415.57 | 0.34
-15 | 5 | 393.59 | 0.35
-14 | 6.8 | 372.87 | 0.37
-13 | 8.6 | 353.34 | 0.39
-12 | 10.4 | 334.92 | 0.41
-11 | 12.2 | 317.55 | 0.43
-10 | 14 | 301.16 | 0.45
-9 | 15.8 | 285.70 | 0.47
-8 | 17.6 | 271.10 | 0.49
-7 | 19.4 | 257.33 | 0.51
-6 | 21.2 | 244.32 | 0.53
-5 | 23 | 232.03 | 0.56
-4 | 24.8 | 220.42 | 0.58
-3 | 26.6 | 209.45 | 0.60
-2 | 28.4 | 199.08 | 0.63
-1 | 30.2 | 189.27 | 0.66
0 | 32 | 180.00 | 0.68
1 | 33.8 | 171.23 | 0.71
2 | 35.6 | 162.93 | 0.74
3 | 37.4 | 155.07 | 0.77
4 | 39.2 | 147.63 | 0.80
5 | 41 | 140.59 | 0.83
6 | 42.8 | 133.92 | 0.86
7 | 44.6 | 127.60 | 0.89
8 | 46.4 | 121.60 | 0.92
9 | 48.2 | 115.93 | 0.95
10 | 50 | 110.54 | 0.98
11 | 51.8 | 105.43 | 1.02
12 | 53.6 | 100.59 | 1.05
13 | 55.4 | 95.99 | 1.08
14 | 57.2 | 91.62 | 1.12
15 | 59 | 87.48 | 1.15
16 | 60.8 | 83.54 | 1.19
17 | 62.6 | 79.80 | 1.22
18 | 64.4 | 76.25 | 1.26
19 | 66.2 | 72.87 | 1.29
20 | 68 | 69.66 | 1.33
21 | 69.8 | 66.61 | 1.37
22 | 71.6 | 63.70 | 1.40
23 | 73.4 | 60.94 | 1.44
24 | 75.2 | 58.31 | 1.47
25 | 77 | 55.81 | 1.51
26 | 78.8 | 53.42 | 1.54
27 | 80.6 | 51.15 | 1.58
28 | 82.4 | 48.99 | 1.62
29 | 84.2 | 46.93 | 1.65
30 | 86 | 44.97 | 1.69
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
31 | 87.8 | 43.10 | 1.72
32 | 89.6 | 41.31 | 1.76
33 | 91.4 | 39.61 | 1.79
34 | 93.2 | 37.99 | 1.82
35 | 95 | 36.44 | 1.86
36 | 96.8 | 34.96 | 1.89
37 | 98.6 | 33.55 | 1.93
38 | 100.4 | 32.21 | 1.96
39 | 102.2 | 30.92 | 1.99
40 | 104 | 29.69 | 2.02
41 | 105.8 | 28.52 | 2.05
42 | 107.6 | 27.40 | 2.08
43 | 109.4 | 26.32 | 2.12
44 | 111.2 | 25.30 | 2.15
45 | 113 | 24.32 | 2.17
46 | 114.8 | 23.38 | 2.20
47 | 116.6 | 22.49 | 2.23
48 | 118.4 | 21.63 | 2.26
49 | 120.2 | 20.81 | 2.29
50 | 122 | 20.02 | 2.31
51 | 123.8 | 19.27 | 2.34
52 | 125.6 | 18.55 | 2.37
53 | 127.4 | 17.86 | 2.39
54 | 129.2 | 17.20 | 2.42
55 | 131 | 16.57 | 2.44
56 | 132.8 | 15.96 | 2.46
57 | 134.6 | 15.38 | 2.49
58 | 136.4 | 14.82 | 2.51
59 | 138.2 | 14.29 | 2.53
60 | 140 | 13.77 | 2.55
61 | 141.8 | 13.28 | 2.57
62 | 143.6 | 12.81 | 2.59
63 | 145.4 | 12.36 | 2.61
64 | 147.2 | 11.92 | 2.63
65 | 149 | 11.51 | 2.65
66 | 150.8 | 11.11 | 2.67
67 | 152.6 | 10.72 | 2.69
68 | 154.4 | 10.35 | 2.70
69 | 156.2 | 10.00 | 2.72
70 | 158 | 9.66 | 2.74
71 | 159.8 | 9.33 | 2.75
72 | 161.6 | 9.01 | 2.77
73 | 163.4 | 8.71 | 2.78
74 | 165.2 | 8.42 | 2.80
75 | 167 | 8.14 | 2.81
76 | 168.8 | 7.87 | 2.83
77 | 170.6 | 7.61 | 2.84
77 | 170.6 | 7.36 | 2.85
78 | 172.4 | 7.12 | 2.87
79 | 174.2 | 6.89 | 2.88
80 | 176 | 6.86 | 2.88
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
81 | 177.8 | 6.67 | 2.89
82 | 179.6 | 6.46 | 2.90
83 | 181.4 | 6.25 | 2.91
84 | 183.2 | 6.05 | 2.92
85 | 185 | 5.86 | 2.93
86 | 186.8 | 5.68 | 2.94
87 | 188.6 | 5.50 | 2.95
88 | 190.4 | 5.33 | 2.96
89 | 192.2 | 5.16 | 2.97
90 | 194 | 5.00 | 2.98
91 | 195.8 | 4.85 | 2.99
92 | 197.6 | 4.70 | 3.00
93 | 199.4 | 4.55 | 3.01
94 | 201.2 | 4.42 | 3.02
95 | 203 | 4.28 | 3.02
96 | 204.8 | 4.15 | 3.03
97 | 206.6 | 4.03 | 3.04
98 | 208.4 | 3.91 | 3.05
99 | 210.2 | 3.79 | 3.05
100 | 212 | 3.68 | 3.06
101 | 213.8 | 3.57 | 3.07
102 | 215.6 | 3.46 | 3.07
103 | 217.4 | 3.36 | 3.08
104 | 219.2 | 3.26 | 3.09
105 | 221 | 3.17 | 3.09
106 | 222.8 | 3.09 | 3.10
107 | 224.6 | 3.00 | 3.10
108 | 226.4 | 2.92 | 3.11
109 | 228.2 | 2.84 | 3.11
110 | 230 | 2.76 | 3.12
111 | 231.8 | 2.68 | 3.12
112 | 233.6 | 2.60 | 3.13
113 | 235.4 | 2.53 | 3.13
114 | 237.2 | 2.46 | 3.14
115 | 239 | 2.39 | 3.14
116 | 240.8 | 2.33 | 3.14
117 | 242.6 | 2.26 | 3.15
118 | 244.4 | 2.20 | 3.15
119 | 246.2 | 2.14 | 3.16
120 | 248 | 2.08 | 3.16
121 | 249.8 | 2.03 | 3.16
122 | 251.6 | 1.97 | 3.17
123 | 253.4 | 1.92 | 3.17
124 | 255.2 | 1.87 | 3.17
125 | 257 | 1.82 | 3.18
126 | 258.8 | 1.77 | 3.18
127 | 260.6 | 1.72 | 3.18
128 | 262.4 | 1.68 | 3.19
129 | 264.2 | 1.63 | 3.19
130 | 266 | 1.59 | 3.19

## Slide 48
18/30
ESI Unitary System Troubleshooting
Display
YES
Check whether TF sensor is seated to the specified location and connected to CN22 on the main control board.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor B*.
YES
NO
Replace the faulty sensor *Note
Check whether there are other heat sources around sensor
NO
YES
Remove all the other heat source
Replace the main control board
Module temperature sensor fault (TF)
Error definition:
The module temperature sensor (TF) is short circuit or open circuit.
Possible causes:
Damaged main control board
Loose connection at port on main control board.
Temperature sensor failure
There are other heat sources around the sensor
NO
Note:
TF sensor is affixed to the heat sink behind the main control board. It cannot be replaced. In the case of a faulty sensor the entire board must be replaced.

## Slide 49
Board Location CN22
PC Module Temperature Sensor (Radiator Sensor)
(TF) Main Board Temperature Sensor
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
-20 | -4 | 517.84 | 0.27
-19 | -2.2 | 489.93 | 0.29
-18 | -0.4 | 463.65 | 0.30
-17 | 1.4 | 438.89 | 0.32
-16 | 3.2 | 415.57 | 0.34
-15 | 5 | 393.59 | 0.35
-14 | 6.8 | 372.87 | 0.37
-13 | 8.6 | 353.34 | 0.39
-12 | 10.4 | 334.92 | 0.41
-11 | 12.2 | 317.55 | 0.43
-10 | 14 | 301.16 | 0.45
-9 | 15.8 | 285.70 | 0.47
-8 | 17.6 | 271.10 | 0.49
-7 | 19.4 | 257.33 | 0.51
-6 | 21.2 | 244.32 | 0.53
-5 | 23 | 232.03 | 0.56
-4 | 24.8 | 220.42 | 0.58
-3 | 26.6 | 209.45 | 0.60
-2 | 28.4 | 199.08 | 0.63
-1 | 30.2 | 189.27 | 0.66
0 | 32 | 180.00 | 0.68
1 | 33.8 | 171.23 | 0.71
2 | 35.6 | 162.93 | 0.74
3 | 37.4 | 155.07 | 0.77
4 | 39.2 | 147.63 | 0.80
5 | 41 | 140.59 | 0.83
6 | 42.8 | 133.92 | 0.86
7 | 44.6 | 127.60 | 0.89
8 | 46.4 | 121.60 | 0.92
9 | 48.2 | 115.93 | 0.95
10 | 50 | 110.54 | 0.98
11 | 51.8 | 105.43 | 1.02
12 | 53.6 | 100.59 | 1.05
13 | 55.4 | 95.99 | 1.08
14 | 57.2 | 91.62 | 1.12
15 | 59 | 87.48 | 1.15
16 | 60.8 | 83.54 | 1.19
17 | 62.6 | 79.80 | 1.22
18 | 64.4 | 76.25 | 1.26
19 | 66.2 | 72.87 | 1.29
20 | 68 | 69.66 | 1.33
21 | 69.8 | 66.61 | 1.37
22 | 71.6 | 63.70 | 1.40
23 | 73.4 | 60.94 | 1.44
24 | 75.2 | 58.31 | 1.47
25 | 77 | 55.81 | 1.51
26 | 78.8 | 53.42 | 1.54
27 | 80.6 | 51.15 | 1.58
28 | 82.4 | 48.99 | 1.62
29 | 84.2 | 46.93 | 1.65
30 | 86 | 44.97 | 1.69
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
31 | 87.8 | 43.10 | 1.72
32 | 89.6 | 41.31 | 1.76
33 | 91.4 | 39.61 | 1.79
34 | 93.2 | 37.99 | 1.82
35 | 95 | 36.44 | 1.86
36 | 96.8 | 34.96 | 1.89
37 | 98.6 | 33.55 | 1.93
38 | 100.4 | 32.21 | 1.96
39 | 102.2 | 30.92 | 1.99
40 | 104 | 29.69 | 2.02
41 | 105.8 | 28.52 | 2.05
42 | 107.6 | 27.40 | 2.08
43 | 109.4 | 26.32 | 2.12
44 | 111.2 | 25.30 | 2.15
45 | 113 | 24.32 | 2.17
46 | 114.8 | 23.38 | 2.20
47 | 116.6 | 22.49 | 2.23
48 | 118.4 | 21.63 | 2.26
49 | 120.2 | 20.81 | 2.29
50 | 122 | 20.02 | 2.31
51 | 123.8 | 19.27 | 2.34
52 | 125.6 | 18.55 | 2.37
53 | 127.4 | 17.86 | 2.39
54 | 129.2 | 17.20 | 2.42
55 | 131 | 16.57 | 2.44
56 | 132.8 | 15.96 | 2.46
57 | 134.6 | 15.38 | 2.49
58 | 136.4 | 14.82 | 2.51
59 | 138.2 | 14.29 | 2.53
60 | 140 | 13.77 | 2.55
61 | 141.8 | 13.28 | 2.57
62 | 143.6 | 12.81 | 2.59
63 | 145.4 | 12.36 | 2.61
64 | 147.2 | 11.92 | 2.63
65 | 149 | 11.51 | 2.65
66 | 150.8 | 11.11 | 2.67
67 | 152.6 | 10.72 | 2.69
68 | 154.4 | 10.35 | 2.70
69 | 156.2 | 10.00 | 2.72
70 | 158 | 9.66 | 2.74
71 | 159.8 | 9.33 | 2.75
72 | 161.6 | 9.01 | 2.77
73 | 163.4 | 8.71 | 2.78
74 | 165.2 | 8.42 | 2.80
75 | 167 | 8.14 | 2.81
76 | 168.8 | 7.87 | 2.83
77 | 170.6 | 7.61 | 2.84
77 | 170.6 | 7.36 | 2.85
78 | 172.4 | 7.12 | 2.87
79 | 174.2 | 6.89 | 2.88
80 | 176 | 6.86 | 2.88
Temp. (°C) | Temp. (°F) | Resistance (KΩ) | Voltage (V)
81 | 177.8 | 6.67 | 2.89
82 | 179.6 | 6.46 | 2.90
83 | 181.4 | 6.25 | 2.91
84 | 183.2 | 6.05 | 2.92
85 | 185 | 5.86 | 2.93
86 | 186.8 | 5.68 | 2.94
87 | 188.6 | 5.50 | 2.95
88 | 190.4 | 5.33 | 2.96
89 | 192.2 | 5.16 | 2.97
90 | 194 | 5.00 | 2.98
91 | 195.8 | 4.85 | 2.99
92 | 197.6 | 4.70 | 3.00
93 | 199.4 | 4.55 | 3.01
94 | 201.2 | 4.42 | 3.02
95 | 203 | 4.28 | 3.02
96 | 204.8 | 4.15 | 3.03
97 | 206.6 | 4.03 | 3.04
98 | 208.4 | 3.91 | 3.05
99 | 210.2 | 3.79 | 3.05
100 | 212 | 3.68 | 3.06
101 | 213.8 | 3.57 | 3.07
102 | 215.6 | 3.46 | 3.07
103 | 217.4 | 3.36 | 3.08
104 | 219.2 | 3.26 | 3.09
105 | 221 | 3.17 | 3.09
106 | 222.8 | 3.09 | 3.10
107 | 224.6 | 3.00 | 3.10
108 | 226.4 | 2.92 | 3.11
109 | 228.2 | 2.84 | 3.11
110 | 230 | 2.76 | 3.12
111 | 231.8 | 2.68 | 3.12
112 | 233.6 | 2.60 | 3.13
113 | 235.4 | 2.53 | 3.13
114 | 237.2 | 2.46 | 3.14
115 | 239 | 2.39 | 3.14
116 | 240.8 | 2.33 | 3.14
117 | 242.6 | 2.26 | 3.15
118 | 244.4 | 2.20 | 3.15
119 | 246.2 | 2.14 | 3.16
120 | 248 | 2.08 | 3.16
121 | 249.8 | 2.03 | 3.16
122 | 251.6 | 1.97 | 3.17
123 | 253.4 | 1.92 | 3.17
124 | 255.2 | 1.87 | 3.17
125 | 257 | 1.82 | 3.18
126 | 258.8 | 1.77 | 3.18
127 | 260.6 | 1.72 | 3.18
128 | 262.4 | 1.68 | 3.19
129 | 264.2 | 1.63 | 3.19
130 | 266 | 1.59 | 3.19

## Slide 50
19/30
ESI Unitary System Troubleshooting
Display
2
1
High pressure sensor
red
White
black
High pressure sensor fault (HP)
1.Error definition and method to check:
The high pressure sensor is open or shorted.
The voltage between CN10 pin(1) and (2) is not in the range 0.59~4.76VDC.
CN10
5V
3
Measure voltage within this space (High Pressure Sensor Voltage Characteristics D*)
2.Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged high pressure sensor
Too little refrigerant remains in the system.
IC A/D
input
GND
YES
NO
Is the high pressure sensor connected to CN10?
Reconnect the sensor
Are the service valves opened?
YES
NO
Open stop valves
Low pressure at gas stop valve to malfunction is 24.5 psig.
NO
YES
Check any refrigerant clogging and shortage.
Connect a gauge on service valve to test high pressure, check whether the pressure transduction is measuring properly?
NO
Replace the pressure sensor
Replace the main control board
YES
Cycle power the unit, can it operate under backup running?
NO
Check the cable connector
YES

## Slide 51
High Pressure Sensor
(HP) High Pressure Sensor
High pressure (MPa) | High pressure (psig) | Resistance (KΩ) | Output voltage(V)
0.1 | 14.5 | 60.60 | 0.59
0.2 | 29.0 | 51.74 | 0.67
0.3 | 43.5 | 44.90 | 0.76
0.4 | 58.0 | 39.47 | 0.85
0.5 | 72.5 | 35.05 | 0.93
0.6 | 87.0 | 31.38 | 1.02
0.7 | 101.5 | 28.29 | 1.11
0.8 | 116.0 | 25.64 | 1.20
0.9 | 130.5 | 23.36 | 1.28
1.0 | 145.0 | 21.36 | 1.37
1.1 | 159.5 | 19.61 | 1.46
1.2 | 174.0 | 18.05 | 1.54
1.3 | 188.5 | 16.66 | 1.63
1.4 | 203.0 | 15.41 | 1.72
1.5 | 217.5 | 14.27 | 1.80
1.6 | 232.0 | 13.25 | 1.89
1.7 | 246.5 | 12.31 | 1.98
1.8 | 261.0 | 11.45 | 2.07
1.9 | 275.5 | 10.66 | 2.15
2.0 | 290.0 | 9.94 | 2.24
2.1 | 304.5 | 9.26 | 2.33
2.2 | 319.0 | 8.64 | 2.41
2.3 | 333.5 | 8.06 | 2.50
2.4 | 348.0 | 7.52 | 2.59
2.5 | 362.5 | 7.01 | 2.67
2.6 | 377.0 | 6.54 | 2.76
2.7 | 391.5 | 6.09 | 2.85
2.8 | 406.0 | 5.67 | 2.93
2.9 | 420.5 | 5.28 | 3.02
3.0 | 435.0 | 4.90 | 3.11
High pressure (MPa) | High pressure (psig) | Resistance (KΩ) | Output voltage(V)
3.1 | 449.5 | 4.55 | 3.20
3.2 | 464.0 | 4.22 | 3.28
3.3 | 478.5 | 3.90 | 3.37
3.4 | 493.0 | 3.60 | 3.46
3.5 | 507.5 | 3.31 | 3.54
3.6 | 522.0 | 3.04 | 3.63
3.7 | 536.5 | 2.78 | 3.72
3.8 | 551.0 | 2.53 | 3.80
3.9 | 565.5 | 2.30 | 3.89
4.0 | 580.0 | 2.07 | 3.98
4.1 | 594.5 | 1.85 | 4.07
4.2 | 609.0 | 1.65 | 4.15
4.3 | 623.5 | 1.45 | 4.24
4.4 | 638.0 | 1.26 | 4.33
4.5 | 652.5 | 1.07 | 4.41
4.6 | 667.0 | 0.90 | 4.50
4.7 | 681.5 | 0.73 | 4.59
4.8 | 696.0 | 0.56 | 4.67
4.9 | 710.5 | 0.40 | 4.76
Board Location C10

## Slide 52
20/30
ESI Unitary System Troubleshooting
Display
3
2
1
Low pressure sensor
red
White
black
Low pressure sensor fault (LP)
1.Error definition and method to check:
The low pressure sensor is open or shorted.
The voltage between CN9 pin(1) and (2) is not in the range 0.70~4.50VDC.
CN9
5V
IC A/D
input
GND
YES
Measure voltage within this space (Low Pressure Sensor Voltage Characteristics C*)
2.Possible causes:
Damaged main control board
Loose connection at port on main control board.
Damaged low pressure sensor
Too little refrigerant remains in the system.
NO
Is the low pressure sensor connected to CN9?
Reconnect the sensor
Are the service valves opened?
YES
NO
Open stop valves
Low pressure at gas stop valve to malfunction is 24.5 psig.
NO
YES
Check any refrigerant clogging and shortage.
Connect a gauge on service valve to test low pressure, check whether the pressure transduction is measuring properly?
NO
Replace the pressure sensor
Replace the main control board
YES
Cycle power the unit, can it operate under backup running?
NO
Check the cable connector
YES

## Slide 53
Low Pressure Sensor
(LP) Low Pressure Sensor
Low pressure (MPa) | Low pressure (psig) | Resistance (KΩ) | Output voltage(V)
0.10 | 14.5 | 49.51 | 0.70
0.11 | 16 | 47.91 | 0.72
0.12 | 17.4 | 46.40 | 0.74
0.13 | 18.9 | 44.97 | 0.76
0.14 | 20.3 | 43.61 | 0.78
0.15 | 21.8 | 42.32 | 0.80
0.16 | 23.2 | 41.09 | 0.82
0.17 | 24.7 | 39.92 | 0.84
0.18 | 26.1 | 38.80 | 0.86
0.19 | 27.6 | 37.74 | 0.88
0.21 | 30.5 | 35.74 | 0.92
0.22 | 31.9 | 34.81 | 0.94
0.23 | 33.4 | 33.92 | 0.96
0.24 | 34.8 | 33.06 | 0.98
0.26 | 37.7 | 31.45 | 1.02
0.27 | 39.2 | 30.69 | 1.04
0.29 | 42.1 | 29.25 | 1.08
0.30 | 43.5 | 28.58 | 1.10
0.32 | 46.4 | 27.29 | 1.14
0.33 | 47.9 | 26.68 | 1.16
0.35 | 50.8 | 25.52 | 1.20
0.37 | 53.7 | 24.44 | 1.24
0.38 | 55.1 | 23.92 | 1.26
0.40 | 58 | 22.94 | 1.30
0.42 | 60.9 | 22.01 | 1.34
0.44 | 63.8 | 21.14 | 1.38
0.46 | 66.7 | 20.32 | 1.42
0.48 | 69.6 | 19.54 | 1.46
0.50 | 72.5 | 18.81 | 1.50
0.52 | 75.4 | 18.11 | 1.54
0.54 | 78.3 | 17.45 | 1.58
0.56 | 81.2 | 16.82 | 1.62
0.58 | 84.1 | 16.22 | 1.66
0.61 | 88.5 | 15.37 | 1.72
0.63 | 91.4 | 14.84 | 1.76
0.65 | 94.3 | 14.33 | 1.80
Low pressure (MPa) | Low pressure (psig) | Resistance (KΩ) | Output voltage(V)
0.68 | 98.6 | 13.61 | 1.86
0.70 | 102 | 13.15 | 1.90
0.73 | 106 | 12.50 | 1.96
0.76 | 110 | 11.89 | 2.02
0.78 | 113 | 11.50 | 2.06
0.81 | 117 | 10.95 | 2.12
0.84 | 122 | 10.43 | 2.18
0.87 | 126 | 9.93 | 2.24
0.90 | 131 | 9.46 | 2.30
0.93 | 135 | 9.02 | 2.36
0.96 | 139 | 8.59 | 2.42
0.99 | 144 | 8.19 | 2.48
1.02 | 148 | 7.81 | 2.54
1.06 | 154 | 7.32 | 2.62
1.09 | 158 | 6.98 | 2.68
1.13 | 164 | 6.54 | 2.76
1.16 | 168 | 6.23 | 2.82
1.20 | 174 | 5.84 | 2.90
1.24 | 180 | 5.46 | 2.98
1.27 | 184 | 5.20 | 3.04
1.31 | 190 | 4.86 | 3.12
1.35 | 196 | 4.53 | 3.20
1.39 | 202 | 4.23 | 3.28
1.43 | 207 | 3.93 | 3.36
1.48 | 215 | 3.59 | 3.46
1.52 | 220 | 3.32 | 3.54
1.56 | 226 | 3.07 | 3.62
1.61 | 233 | 2.77 | 3.72
1.65 | 239 | 2.55 | 3.80
1.70 | 247 | 2.27 | 3.90
1.75 | 254 | 2.02 | 4.00
1.80 | 261 | 1.77 | 4.10
1.85 | 268 | 1.54 | 4.20
1.90 | 276 | 1.31 | 4.30
1.95 | 283 | 1.10 | 4.40
2.00 | 290 | 0.90 | 4.50
Board Location CN9

## Slide 54
EEV
(EEV) Electronic Expansion Valve
Saginomiya – 5 wire
Grey – Orange = 46 ohms
Grey – Red = 46 ohms
Grey – Yellow = 46 ohms
Grey – Black = 46 ohms
Readings should be +/- 4 Ohms
Board Location CN13

## Slide 55
23/30
ESI Unitary System Troubleshooting
Abnormal switch alarm for 4-way valve
1.Error definition:
4-way valve switch incompletely after defrost operation or from cooling mode. If TH ≥ TL+5.4F and TH ≥ TA+5.4F, report this alarm.
2.Possible causes:
Damaged 4-way valve
Damaged main control board
Abnormal voltage of power supply(too low voltage)
Temperature sensor(TH) failure
4-way valve is set up power on when cooling mode.
Display
YES
NO
Is the output on connector CN14 (4-way valve) 220VAC in heating mode?
Replace the main control board
Is the gas pipe close to service valve hot?
NO
YES
Check whether TH temperature sensor is failed.
Change the coil of 4-way valve and restart the system, does the problem remain?
YES
NO
Normal control
Recover the refrigerant and replace the 4-way valve body.
NO
YES
The power supply voltage is less than 175VAC.
Contact agency supplying power to verify that they are sending the correct voltage.
YES
Replace the main control board, is the alarm disappears?
NO

## Slide 56
Reversing Valve
4 Way Valve Solenoid Coil
Board Location CN14

## Slide 57
21/30
ESI Unitary System Troubleshooting
Display
Communication fault between main chip and INV drive chip
YES
Replace the main control board
NO
External factor other than malfunction(e.g. noise interference).
Error definition and method to check:
Communication fault between the main control chip and inverter chip.
Possible causes:
Loose connection at CN21 terminal.
Damaged main control board
Turn off the power supply until the LED display lights off. Unplug the cable from terminal CN21, Restart power to check if the fault remains.
CN21

## Slide 58
Key Product Components
Connecting Harness between Main Chip and Inverter Chip
CN 21
Remove to gain access

## Slide 59
ESI (Ultra) Service Manual
www.ecoer.com
60/68
NOTE: Normal resistance for compressor
3-phase resistance (UV, UW, VW) for compressor is less than 5Ω.
The insulation resistance (any phase to Ground) for compressor is greater than 100KΩ.
Display
or
Compressor INV module protection
YES
NO
YES
NO
NO
YES
YES
NO
YES
NO
Turn off the power supply to replace the main control board. Restart the unit, does the error code disappear?
NO
YES
Back to normal
Replace the compressor
Clean the terminal
Are compressor terminals damaged or corroded?
Replace the compressor
Is the compressor open-circuited? *NOTE
Reconnect the wiring
Are the compressor wires (U/V/W) securely connected?
Replace the indoor coil
Has the micro channel coil been used for heat pump?
Check power supply voltage is not in the range of 187~253VAC.
Contact power supply agency to verify that they are sending the correct voltage.

## Slide 60
Compressor
Connecting Harness between Main Chip and Inverter Chip
Remove to gain access
Remove
Remove (3) power wirers

## Slide 61
Key Product Components
U - V less than 5 ohms
U - W less than 5 ohms
V - W less than 5 ohms
Readings should be +/- 10% between each reading

## Slide 62
ESI (Ultra) Service Manual
www.ecoer.com
59/68
1. Error definition:
Code | LED Display |  |  | Definition
C0 |  |  |  | Critical over-voltage fault
C1 |  |  |  | DC bus over-voltage protection
C2 |  |  |  | DC bus under-voltage protection
C3 |  |  |  | Over-current protection
C4 |  |  |  | Zero speed fault
C5 |  |  |  | Synchronization - PwmsyncErr
C6 |  |  |  | Phase loss protection for 3-phase lines U, V, W in compressor-PhslossFlt
C7 |  |  |  | Compressor speed inconsistent fault
C8 |  |  |  | Compressor speed instability
C9 |  |  |  | Compressor speed difference between given transient variation and actual operation
CA |  |  |  | AC over-voltage protection
CB |  |  |  | AC under-voltage protection
CC |  |  |  | PFC error
E0: System locks up when C0~CA has occurred three times in 60 minutes.
2. Possible causes:
Abnormal power supply voltage
Power supply disconnected (C2/C7/C9 or C2/C3/C7 report at the same time)
Dirty compressor terminal or damaged compressor
Damaged main control board
Micro channel coil has been used for heat pump
Display
or
Compressor INV module protection

## Slide 63
3/30
ESI Unitary System Troubleshooting
No Display
YES
NO
Replace the noise filter
or
YES
Replace the inductance
NO
NO
NO
The unit energized but the digital
tube shows nothing
Error definition:
No display on main control board even though the unit has been powered ON.
Possible causes:
Damaged noise filter.
Damaged inductance.
Loose connection at port on main control board.
Damaged pressure sensor.
Damaged fan motor.
Damaged main control board.
Note: Confirm the power supply prior to go to the following steps.
Fasten screws for it
Turn off the unit for five minutes to fasten the screw.
Replace the fan motor
YES
Replace the main control board
Replace the low pressure
sensor
Is the voltage between CN18 and CN19 (i.e. L1&L2) 208~230VAC?
Turn off the power supply for five minutes to confirm if cables connected to P2 and P3 terminals are securely fastened by screws.
Use multi-meter to check whether the inductance is open.
Whether the cable connected to CN21 terminal behind the black plastic is firmly fastened.
Turn off the power supply for five minutes, unplug fan motor from terminal CN8. Turn on the power supply and the display lights ON.
Unplug low pressure sensor at terminal CN9, cycle the power and the display lights ON.
Unplug high pressure sensor at terminal CN10, cycle the power and the display lights ON.
YES
YES
NO
NO
YES
Replace the high pressure sensor
YES
NO

## Slide 64
ESI (Ultra) Service Manual 12/68 www.ecoer.com
    Protection controls
      High pressure protection control
High pressure (HP) protection control is used to prevent extremely high pressures in the system and protect the compressor.
HP≥C
HP<D
HP<D
HP≥B
After 15 sec.
HP≥B
HP≥A
High pressure abnormal standby
Compressor Speed is Maintained
Normal operation
(Upper limit compressor step = Max. step)
Compressor Speed Decreased
Current step maintained
HP<D
and
Restart permission=ON
Symbol | EODA18H-2436/4860 | 
 | Cooling | Heating
A | 545psig [3.8MPa] | 545psig [3.8MPa]
B | 493psig [3.4MPa] | 479psig [3.3MPa]
C | 479psig [3.3MPa] | 450psig [3.1MPa]
D | 464psig [3.2MPa] | 421psig [2.9MPa]
Compressor restarts

## Slide 65
4/30
ESI Unitary System Troubleshooting
Display
High pressure protection
NO
or
NO
Replace the main control board
YES
Error definition:
P1: The detected high pressure is no less than 566psig.
E1: System locks up when P1 has occurred six times within 3 hours.
Possible causes:
Service valves are closed.
The system has been severely over-charged.
Indoor air filter is dirty
Dirty heat exchanger of outdoor unit in cooling mode.
The refrigerant blocked in high pressure zone because of damaged TXV in cooling mode or damaged EEV in heating mode.
G signal is lost resulting in indoor unit FAN=OFF in heating mode.
Damaged high pressure sensor.
Damaged main control board.
Note: Connect a pressure gauge to liquid stop valve in cooling mode, gas stop valve in heating mode. Compare the value difference between gauged pressure and the transduced one by sensor.
NO
Replace the high pressure
sensor
YES
YES
Cooling mode:
Check if the TXV of indoor unit is dirty plugging.
Heating mode:
Check if the EEV of outdoor unit is dirty plugging.
Use AUTO charge mode to check whether there is too much refrigerant in the system.
Replace the main control board if the protection happens again with proper refrigerant amount.
Check visible parts for the system 1) Closed service valve; 2) Dirty heat exchanger; 3) Dirty air filter; 4) FAN is not operating |  |  | 
 | YES |  | 
Satisfy any contents above. |  |  | Correct specific point
Can the pressure transduce properly based on High Pressure Sensor Voltage Characteristics D*.
Is the high pressure close to 566psig before protection?
Whether the low pressure has been evacuated?
NO

## Slide 66
5/30
ESI Unitary System Troubleshooting
Display
Low pressure protection in cooling
mode
or
NO
YES
NO
Replace the low pressure sensor
Can the pressure transduce measure properly according to Low Pressure Sensor Voltage Characteristics C*.
Correct specific point
1.Error definition:
P2: The detected low pressure in cooling mode is less than 24.5psig. E2: System locks up when P2 has occurred six times within 3 hours. 2.Possible causes:
Service valves are closed.
Dirty air filter or indoor heat exchanger
Outside temperature is lower than 23F (i.e. low ambient temperature cooling)
Too little refrigerant in the system.
Defective indoor R410A TXV.
G signal is lost resulting in indoor unit FAN=OFF.
Damaged low pressure sensor.
Damaged main control board.
Note：Connect a pressure gauge to gas stop valve, compare the difference between the gauged
pressure and the transduced one by low pressure sensor.
Check visible parts for the system
  Closed service valve; 2) Clogged indoor heat exchanger; 3) Dirty air filter; 4) Fan is not operating
YES
Satisfy any contents above.
NO
Replace the main control board
YES
Is the low pressure close to 24.5psig before protection?
YES
Check whether the TXV of indoor unit is dirty plugging.
Use AUTO charge mode to check whether there is too little refrigerant in the system.
Replace the main control board if the protection happens again with proper refrigerant amount.
Whether the low pressure has been evacuated?
NO

## Slide 67
6/30
ESI Unitary System Troubleshooting
Discharge temperature protection
YES
or
Error definition:
P3: The maximum detected discharge temperature(TD) is no less than 248F.
E3: System locks up when P3 has occurred six times within 3 hours.
Possible causes:
Too little refrigerant remains in the system.
Dirty plugging of TXV(indoor unit).
Damaged discharge temperature sensor.
Damaged main control board.
NO
NO
Reset the sensor or reconnect the wire
YES
Replace the faulty sensor
YES
Check the refrigerant amounts
NO
Replace the compressor
Display
Are the stop valves of outdoor unit open?
NO
Open the stop valve
Check whether the discharge temperature sensor is properly seated on the discharge pipe and securely connected to CN7 terminal on the main control board.
Check whether the Resistance of Temperature sensor B* is correct.
Unplug TD sensor from CN7 and cycle the power. Can it operate under backup running?
YES
Is there abnormal sound or vibration for compressor?
YES
Replace the main control board
NO

## Slide 68
7/30
ESI Unitary System Troubleshooting
Discharge temperature sensor is disconnected or damaged
Error definition:
When TD<TC-9F for 20 minutes, or the suction superheat(SH) is no less than 9F with TD<TL-9F lasts 20 minutes.
TC: The saturation temperature of high pressure
Possible causes:
Discharge temperature (TD) sensor is disconnected or damaged.
Damaged main control board
Loose connection at port on main control board.
There are other heat sources around the sensor
Display
YES
NO
Check whether TD sensor is seated to the compressor discharge pipe
and securely connected to CN7 terminal on the main control board.
Reset and reconnect the TD sensor
Check whether the Resistance of Temperature sensor B* is correct.
YES
NO
Replace the faulty sensor
Check whether there are other heat sources around sensor.
NO
YES
Remove all the other heat source
Unplug TD sensor from CN7 and cycle the power. Can it operate under
backup running?
NO
Replace the main control board
Replace the TD sensor
YES

## Slide 69
8/30
ESI Unitary System Troubleshooting
Module temperature protection
or
Error definition:
P5: The detected value of module temperature (TF) is no less than specific value.
2~3Ton: 181F
4~5Ton: 176F in cooling mode 167F in heating mode
E5: System locks up when P5 has occurred six times within 3 hours.
Possible causes:
Clogged fin of radiator resulting in poor heat transfer
Misjudgment caused by resistance drift of TF sensor
Dirty and blocked heat exchanger for the ODU
Damaged TF sensor
Damaged main control board.
Display
YES
NO
Does the heat discharge channel for outside exchanger and the fan work properly?
Exclude heat discharge factor
Is the heat exchanger in the back of main control board dirty or corroded resulting in poor performance.
NO
YES
Remove the dirty or blocked materials or replace the PCB.
Check whether the resistance of sensor is in the range of Temperature sensor B*.
YES
NO
Replace the TF sensor
*Note
Replace the main control board
Note:
TF senor has been laid inside the assembly control box with silicon gel contacting the radiator . It’s required to replace the main control board in this case.

## Slide 70
9/30
ESI Unitary System Troubleshooting
Over-current protection for compressor
or
Error definition:
P6: The detected compressor current is over the maximum allowable value.
2~3Ton: 16A
4~5Ton: 20A
E6: System locks up when P6 has occurred six times within 3 hours.
Possible causes:
Abnormal power supply voltage
Too much refrigerant in the system resulting in liquid slugging at compressor.
Damaged main control board.
Indoor unit is suddenly powered off.
Damaged compressor.
Display
NO
YES
The power supply voltage is less than175VAC.
Contact agency supplying power to verify that they are sending the correct voltage.
Are the compressor wirings(U/V/W) connected correctly?
YES
NO
Reconnect the compressor wiring
Check whether the compressor is open-circuited. *Note
NO
YES
Replace the compressor
Can the system restarted when the differential of high pressure and low pressure is less than 29psi?
YES
Check the stop valve state and
occlusion of refrigerant pipe
Replace the main control board
NO
Note: Normal resistance for compressor
3-phase resistance for compressor is less than 5Ω.
The insulation resistance for compressor is greater than 100KΩ.

## Slide 71
10/30
ESI Unitary System Troubleshooting
Liquid slugging protection
or
Error definition:
This control is to prevent compressor from damaging because of liquid slugging. When SH is less than 9.0F as well as discharge superheat (DSH=TD-TC) is less than 14.4F for 30 minutes, starting to accumulate the liquid slugging time. Report the error code P7 once if it lasts for 60 minutes.
E7: System locks up when P7 has occurred three times in 5 hours.
Possible causes:
Damaged or improper TXV for indoor unit in cooling mode.
Damaged discharge temperature (TD) sensor
Excess refrigerant charge
Damaged EEV of outdoor unit in heating mode.
Damaged main control board.
Cooling mode
Connect a pressure gauge at the gas stop valve to calculate suction superheat(SH).
Display
YES
NO
Has the proper R410A TXV been used for indoor unit?
R410A TXV is required for this inverter system
Is the superheat at gas stop valve larger than 6F.
YES
NO
Check indoor unit (e.g. TXV has no adjusting, fan does not work, filter is dirty and so on.) and refrigerant charge.
YES
Check the pressure transduction based on Low Pressure Sensor NO
Voltage Characteristics C*. Does the low pressure sensor measure normally?
Replace the low pressure sensor
Set high capacity mode and restart the unit, does the error code remain?
NO
Keep running
Replace the main control board
YES
NO
Reset the sensor or reconnect the wire
YES
Check whether the discharge temperature sensor is properly seated on the discharge pipe and securely connected to CN7 terminal on the main control board.

## Slide 72
11/30
ESI Unitary System Troubleshooting
Heating mode
Connect a pressure gauge to liquid stop valve, compare the gauged pressure with the transduced one by high pressure sensor.
YES
NO
Does the EEV cable securely connected to CN13 terminal.
Reconnect the cable
Check the pressure transduction based on High Pressure Sensor Voltage Characteristics D*. Is the value of high pressure sensor detected close to the gauged one?
YES
NO
Replace the high pressure sensor
Set high capacity mode and restart the unit, does the error code remain?
NO
Keep running
Replace the main control board
YES
NO
Reset the sensor or reconnect the wire
YES
Check whether the discharge temperature sensor is properly seated on the discharge pipe and securely connected to CN7 terminal on the main control board.
Lock the liquid stop valve and use test mode 8 (*Note) to fix compressor speed. Recover the refrigerant from outdoor unit to indoor unit side. The EEV cannot be closed if the recover process is failed.
YES
NO
Replace the EEV coil to repeat test mode 8. Change the EEV body if it fails again.
Note: Hold BS4 for 5sec, and press BS2 once in one minute will activate test mode 8.

## Slide 73
12/30
ESI Unitary System Troubleshooting
Display
DC fan motor over-load protection
1.Error definition:
The fan rotation speed is less than 240RPM if it has the running signal.
The rotation speed difference between the detected value and target one is over 200RPM for 3 minutes.
2.Possible causes:
Damaged main control board
Malfunction of fan motor
Disconnected wiring between fan motor and main control board
YES
NO
Is the fan motor cable connected to CN8 on main control board?
Connect the cable
Turn off power supply, check whether the motor shaft is stuck. (Try using tools to rotate the motor manually)
NO
YES
Replace the motor
Replace the main control board
Low compressor voltage protection
Error definition:
P8: The detected compressor voltage by main chip is less than 310VDC. E8: System locks up when P8 has occurred three times in 60 minutes.
Possible causes:
Abnormal power supply voltage
Damaged main control board.
Display
or
YES
Abnormal power supply voltage
Contact agency supplying power to verify that they are sending the correct voltage.
Replace the main control board
NO
NO
Had the IoT gateway successfully communicated with cloud after installation?
Make sure the IoT gateway can work.
YES

## Slide 74
22/30
ESI Unitary System Troubleshooting
Ambient temperature limit operation
or
Error definition and method to check:
H1: The detected ambient temperature is absolutely prohibited for cooling.
TA<14F or ≥140F
H2: The detected ambient temperature is absolutely prohibited for heating.
TA ≥ 86F or TA< forced heating stop temperature set by n01
Possible causes:
The ambient temperature exceeds the set range of operation.
The system is running previous mode
Damaged ambient temperature sensor (TA)
Damaged main control board.
Display
YES
NO
Check whether the ambient temperature sensor (TA) is seated to the specified location and connected to CN2 of PCB.
Reconnect the sensor
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the fault sensor
Check whether there are other heat sources around sensor
NO
YES
Remove all the other heat source
Is the outside temperature within the range of operation
Replace the main control board
NO
It’s normal control to protect the system.
YES
YES
Does the unit running heating mode (compressor=ON) but the thermostat switches to cooling mode, or the unit running cooling mode (compressor=ON) but the thermostat switches to heating mode at that time.
The unit will respond to mode switch after stop for 6 minutes.
NO

## Slide 75
24/30
ESI Unitary System Troubleshooting
Display
Condenser coil temperature sensor is disconnected or damaged
YES
NO
Check whether TH sensor is seated to the heat exchanger pipe and connected to CN4 of PCB.
Reset the sensor or reconnect the cable
Check whether the resistance of sensor is in the range of
Temperature sensor A*.
YES
NO
Replace the faulty sensor
Are there any other heat sources around the sensor?
NO
YES
Remove all the other heat source
Can the system go into back up running?
YES
Replace the sensor
Replace the main control board
NO
Error definition:
The coil temperature sensor (TH) is short circuit or open circuit.
Possible causes:
Damaged main control board
The condenser coil temperature is wrongly seated
Temperature sensor failure
There are other heat sources around the sensor

## Slide 76
25/30
ESI Unitary System Troubleshooting
Display
EEPROM fault
Error definition:
Data cannot be correctly received from the EEPROM, a type of memory component, remembers contents even though the power supply is turned off.
Possible causes:
Damaged main control board
Display
Low voltage alarm
Error definition:
Power supply voltage is less than175VAC.
Possible causes:
Abnormal power supply voltage.
Damaged main control board.
YES
Cycle power for the unit, can the system back to normal?
External interference (e.g. electromagnetic)
Replace the main control board
NO
YES
The power supply voltage is less than 175VAC.
Contact agency supplying power to verify that they are sending the correct voltage.
Replace the main control board
NO

## Slide 77
Key Product Components

## Slide 78
Key Product Components

## Slide 79
Key Product Components

## Slide 80
Key Product Components

## Slide 81
Key Product Components

## Slide 82
Ecoer startup Check List

## Slide 83
Air Handler Installation

## Slide 84
1
4
W
A
NOTE: 25’’ CLEARANCE IS REQUIRED IN THE FRONT OF THE UNIT FOR FILTER AND COIL MAINTENANCE.
D
10-5/16
FLANGES ARE PROVIDED FOR FIELD INSTALLATION
Breaker Switch (Electric heat only)
High voltage connection
7/8’’, 1-3/32’’, 1-23/32’’ DIA knockouts
KNOCKOUTS FOR ELECTRICAL WIRING CONNECTION ARE DISTRIBUTED ON THE TOP AND
EITHER SIDES.
H
Sweat Suction Line
Sweat Liquid Line
Auxiliary drain connection 3/4’’ Female pipe thread (NPT)
Inlet (Front View)
Primary drainconnection 3/4’’ Female pipe thread (NPT)
Figure 2-1 Unit Dimensions
Inlet (Left Side View)
Model Number | Dimensions (in.) |  |  |  |  | 
 | H | W | D | A | Liquid Line | Suction Line
24 / 36 | 46-1/2 | 21 | 21 | 19-1/4 | 3/8 | 3/4
48 / 60 | 56 | 24-1/2 | 21 | 22-3/4 | 3/8 | 7/8
Air Handler Dimensions

## Slide 85
1
Evaporator Coil

## Slide 86
1
Blower Motor
Mounting Screws

## Slide 87
1
Clearances
Horizontal
Vertical

## Slide 88
1
Vertical Up- Flow
Default Orientation

## Slide 89
1
Horizontal Right- Flow
Airflow
Default Orientation

## Slide 90
1
Vertical Down- Flow
Invert Air Handler 180 Degrees
Invert A-Coil 180 Degrees

## Slide 91
1
Horizontal Left - Flow
Invert Air Handler 180 Degrees
Invert A-Coil 180 Degrees

## Slide 92
1
Air Flow 2 ton, 3 ton
Model Number | Motor Speed |  |  |  |  |  |  |  |  |  |  | 
 |  |  | External Static Pressure-Inches W.C.[KPa] |  |  |  |  |  |  |  |  | 
 |  |  | 0 [0] | 0.1 [.02] | 0.16 [.04] | 0.2 [.05] | 0.3 [.07] | 0.4 [.10] | 0.5 [.12] | 0.6 [.15] | 0.7 [.17] | 0.8 [.20]
24 | Tap (5) | SCFM | 1062 | 1031 | 998 | 981 | 947 | 901 | 869 | 823 | 789 | 742
 |  | Watts | 184 | 195 | 201 | 203 | 213 | 222 | 228 | 238 | 242 | 252
 | Tap (4) | SCFM | 959 | 921 | 890 | 873 | 836 | 786 | 751 | 706 | 677 | 622
 |  | Watts | 138 | 145 | 152 | 156 | 162 | 171 | 178 | 188 | 196 | 204
 | Tap (3)- factory | SCFM | 855 | 825 | 790 | 769 | 733 | 679 | 646 | 595 | 560 | 494
 |  | Watts | 101 | 111 | 118 | 120 | 126 | 134 | 141 | 151 | 156 | 166
 | Tap (2) | SCFM | 777 | 750 | 712 | 692 | 656 | 599 | 566 | 498 | 466 | 412
 |  | Watts | 80 | 89 | 96 | 98 | 104 | 113 | 119 | 127 | 135 | 145
 | Tap (1) | SCFM | 694 | 663 | 620 | 599 | 562 | 499 | 455 | 390 | --- | ---
 |  | Watts | 60 | 68 | 74 | 76 | 82 | 89 | 95 | 104 | --- | ---
36 | Tap (5) | SCFM | 1455 | 1409 | 1374 | 1355 | 1320 | 1266 | 1229 | 1173 | 1126 | 956
 |  | Watts | 293 | 300 | 306 | 309 | 316 | 326 | 331 | 338 | 346 | 370
 | Tap (4) | SCFM | 1350 | 1302 | 1264 | 1242 | 1206 | 1145 | 1104 | 1038 | 897 | 824
 |  | Watts | 238 | 243 | 254 | 257 | 260 | 271 | 277 | 286 | 303 | 308
 | Tap (3)- factory | SCFM | 1328 | 1281 | 1234 | 1215 | 1179 | 1118 | 1073 | 1007 | 862 | 798
 |  | Watts | 226 | 232 | 239 | 242 | 250 | 259 | 264 | 278 | 292 | 298
 | Tap (2) | SCFM | 1235 | 1171 | 1130 | 1108 | 1062 | 1002 | 955 | 824 | 752 | 713
 |  | Watts | 185 | 189 | 196 | 199 | 205 | 214 | 221 | 238 | 245 | 248
 | Tap (1) | SCFM | 1146 | 1091 | 1044 | 1022 | 982 | 908 | 823 | 748 | 708 | ---
 |  | Watts | 150 | 156 | 163 | 167 | 174 | 184 | 196 | 202 | 207 | ---

## Slide 93
1
Air Flow 4 ton, 5 ton
Model Number | Motor Speed |  |  |  |  |  |  |  |  |  |  | 
 |  |  | External Static Pressure-Inches W.C.[KPa] |  |  |  |  |  |  |  |  | 
 |  |  | 0 [0] | 0.1 [.02] | 0.16 [.04] | 0.2 [.05] | 0.3 [.07] | 0.4 [.10] | 0.5 [.12] | 0.6 [.15] | 0.7 [.17] | 0.8 [.20]
48 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327
60 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327

## Slide 94
Wiring Diagram Version A
Control Board:
L1 208/240/1/60
Heater Plug
Transformer 208/230/24vac
L2 208/240/1/60
Ground
Fuse
Low Voltage 24 Volt
Fan Speed Control
208 Volt Tap. Swap with CN1 (Black) for 208 volt

## Slide 95
1
Wiring Diagram Version B

## Slide 96
1
Changing Fan Speed Medium High, High

## Slide 97
1
Changing Fan Speed Low, Medium Low

## Slide 98
1
Changing Fan Speed
Dip Switch SW 1
Medium Low
Low

## Slide 99
Reduce Fan Speed
Swap
Locking Tab

## Slide 100
1
Changing Fan Speed
Depress tap to remove spade Terminal

## Slide 101
1
Power Supply
Model Number | Voltage-Phase-Hz | Power Supply Wiring Gauge | Motor HP | Motor Steps | Minimum Circuit AMPS. | Fuse (A)
24 | 208/230-1Ph-60Hz | 14 | 1/3 | 5 | 3.0 | 15
36 |  |  | 1/2 |  | 5.2 | 
48 |  |  | 3/4 |  | 7.5 | 
60 |  |  | 3/4 |  | 7.5 | 
Without electric Heat

## Slide 102
1
Wiring Diagram
With Electric Heat
Kit Model | Model Number | Electric Heat (kW) | MIN. Circuit Ampacity |  | MAX. Fuse or Breaker (HACR) Ampacity |  | Fan speed |  |  |  | 
 |  |  | 240 | 208 | 240 | 208 | 1 | 2 | 3 | 4 | 5
E-EHK05 | 24 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | × | ● | ● | ●
E-EHK05 | 36 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | × | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK05 | 48 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | ● | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK20 |  | 10+10 | 49+49 | 43+43 | 60+60 | 50+50 | × | × | × | ● | ●
E-EHK05 | 60 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | ● | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK20 |  | 10+10 | 49+49 | 43+43 | 60+60 | 50+50 | × | × | × | ● | ●

## Slide 103
1
Electric Heat Wiring
Knock out left template for 5, 8, 10KW Heat. Knock out both for 15, 20 KW

## Slide 104
1
Electric Heat Wiring
Remove top cover plate for 5,8,or 10KW heater. Remove both for 15, 20KW

## Slide 105
1
Electric Heat Wiring
STEP 3. Slide the kit into the duct and fasten the element (e.g. attachment and wires).

## Slide 106
1
Electric Heat Wiring

## Slide 107
1
Electric Heat Wiring
CN 1
CN 3
CN 6

## Slide 108
1
Fan Speed Control
EST01, EST02 Ecoer Thermostat

## Slide 109
1
Transformer Basics
Transformers do not generate electrical power; they transfer electrical power from one AC circuit to another using magnetic coupling. The core of the transformer is used to provide a controlled path for the magnetic flux generated in the transformer by the current flowing through the windings, which are also known as coils. There are four primary parts to the basic transformer. The parts include the Input Connection, the Output Connection, the Windings or Coils and the Core.

## Slide 110
1
Transformer Basics
When an input voltage is applied to the primary winding, alternating current starts to flow in the primary winding. As the current flows, a changing magnetic field is set up in the transformer core. As this magnetic field cuts across the secondary winding, alternating voltage is produced in the secondary winding. The ratio between the number of actual turns of wire in each coil is the key in determining the type of transformer and what the output voltage will be. The ratio between output voltage and input voltage is the same as the ratio of the number of turns between the two windings.
A transformers output voltage is greater than the input voltage if the secondary winding has more turns of wire than the primary winding. The output voltage is stepped up, and considered to be a "step-up transformer". If the secondary winding has fewer turns than the primary winding, the output voltage is lower. This is a "step-down transformer".
500 Wraps
Input voltage: 240 Volt
50 Wraps
Output voltage:24 Volt
Vs= Ns*Vp / Np
Vs = Secondary Voltage
Vp = Primary Voltage
Ns = Secondary Wraps
Np = Primary Wraps
Vs = 50*240/500: Vs = 24 volts

## Slide 111
1
Control Wiring

## Slide 112
1
Control Wiring
R
C
G
G2
W1
Y
24 – 30 VAC

## Slide 113
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC

## Slide 114
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
When The thermostat closes contact between R and G, a relay in the air handler is closed resulting in the fan to run.

## Slide 115
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
The C from the air handler also is connected to the C terminal on the heat pump. The Y terminal on the thermostat is connected to the Y on the heat pump. This results in the heat pump running in the heating mode
O Y C W

## Slide 116
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
When the thermostat closes the O contact the heat pump will revert to cooling mode
O Y C W

## Slide 117
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
When the thermostat closes the W2/AUX contact the Aux heat will initiate and run.
O Y C W

## Slide 118
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
The heat pump can as well initiate the Aux heat by closing the contact between O and W.
O Y C W

## Slide 119
1
Control Wiring
R
C
G
G2
W1
24 – 30 VAC
For the Honeywell T10 thermostat to enable the Aux heat, work, it will need a source for the outside temperature either a sensor or WiFi
O Y C W

## Slide 120
1
Control Wiring
R
C
G
Y
W1
24 – 30 VAC
If we substitute the air handler for a furnace, the only change is the thermostat also enables a Y contact on the furnace in order to change the fan speed.
O Y C W

## Slide 121
Low Voltage Wiring
Ecoer Heat Pump, Ecoer Air Handler, Honeywell HZ432, Honeywell T10

## Slide 122
Low Voltage Wiring
Ecoer Heat Pump, Ecoer Furnace, Honeywell HZ432, Honeywell T10

## Slide 123
Low Voltage Wiring
Ecoer Heat Pump, Ecoer air Handler, Hydronic Relay, Honeywell HZ432, Honeywell T10

## Slide 124
Low Voltage Wiring
RIB Relay Wiring
Relay White /Yellow Common
White / Blue W1
Contact Yellow T
Orange T

## Slide 125
Air Handler Service
Evaporator Blower Motor:
L1 208/240/1/60
24 Volt Common
Low Speed 24 volts
L2 208/240/1/60
Ground
Med Low Speed 24 volts
Medium Speed 24 volts
Med High Speed 24 volts
High Speed 24 volts

## Slide 126
Air Handler Service
Evaporator Coil and TXV:
Increase Superheat
Decrease Superheat

## Slide 127
The Art of Duct Work

## Slide 128
Components of Duct System

## Slide 129
Supply Air Flow Capacity

## Slide 130
Basic Guidelines for Ductwork
Supplies are located on outside walls.
Returns are located on inside walls. They should not be in the same area as the furnace, nor should they be located by moisture sources such as kitchens or bathrooms.
Dampers on take-off duct runs allow for adjustments of air distribution.
In order to maintain velocity, reduce duct size.
Never locate ducts at the end of the trunk line run. Last take-off run to be located 12″ – 18″ from end.

## Slide 131
Basic Guidelines for Ductwork
Always stagger take-off ducts by 12″ to maintain pressure.
Use insulated duct or duct board in unheated spaces.
Flexible duct work must be stretched tightly for maximum air flow.
Trunk lines should not exceed 24 feet without reducing
Trunk Supply Velocity should be 700 to 900 fpm
Branch Supply Velocity should be 500 to 700 fpm
Return Velocity should be 500 to 700 fpm
Return duct should be 20% larger than the supply duct

## Slide 132
Basic Guidelines for Ductwork
Abrupt changes in air direction is a leading cause of poor air supply
Flexible duct work must be stretched tightly for maximum air flow.

## Slide 133
Basic Guidelines for Ductwork (Cooling)
Determine CFM for home with the following equation
  CFM = Unit size (in tons) x 400 cfm/ton/home square footage
  Example: Existing unit size: 3 tons
          Square footage of home: 1100 SF2
          CFM = (3 x 400) / 1100
          CFM = 1.09 cfm / ft2

## Slide 134
Basic Guidelines for Ductwork
Room Living 300 ft2 300 / 1100 x 1200 = 327 cfm
Room Bed 1 120 ft2 120 / 1100 x 1200 = 131 cfm
Room Bed 2 120 ft2 120 / 1100 x 1200 = 131 cfm
Room Bed 3 200 ft2 200 / 1100 x 1200 = 218 cfm
Room Kitchen 200 ft2 200 / 1100 x 1200 = 218 cfm
Room Bath 1 100 ft2 100 / 1100 x 1200 = 109 cfm
Room Bath 2 60 ft2 60 / 1100 x 1200 = 60 cfm
      Total 1,100 ft2 1,194 cfm

## Slide 135
Basic Guidelines for Ductwork

## Slide 136
Basic Guidelines for Ductwork
Space Temperature
Outside Temperature
Mixed Temperature
Infiltration

## Slide 137
Basic Guidelines for Ductwork
MA = Mixed air
ST = Space Temperature
OA = Outside air
IA%= ((MA-ST) / (OA-ST))x 100
Infiltration

## Slide 138
Basic Guidelines for Ductwork
Infiltration
MA= 80º
ST = 70º
OA = 95º
IA% = ((80º-70º) / (95º-70º)) x 100
IA% = (10 / 25) x 100
IA% = 40%

## Slide 139
T10 PRO SMART THERMOSTAT WITH REDLINK
33-00462—03
16
IMPORTANT
Erratic temperature readings from a sensor can occur as a result of any of the wiring practices described below. Avoid these practices to assure correct operation. Use shielded cable to reduce interference if rerouting of sensor wiring is not pos- sible.
Be sure wires have a cable separate from the ther- mostat cable.
Do not route temperature sensor wiring with build-
ing power wiring, next to control contactors or near light dimming circuits, electric motors or welding equipment.
Avoid poor wiring connections.
Avoid intermittent or missing building earth ground.
Installer setup (new installation)
After the thermostat has powered up, touch “GET STARTED” on the thermostat.
After selecting the correct option for each setting, Touch NEXT at the bottom of the display to advance
to the next option.
To see a list of all setup parameters, go to "Installer setup (ISU)" starting on page 16. The thermostat dis- plays the ISU name.
To finish setup and save your settings, TOUCH “Done” in the upper left of display
Installer setup (revising settings)
If this is not a new installation and you want to access the Installer setup to change settings:
1. Touch the menu icon (3 horizontal lines at bottom of display)
Scroll down and touch “Thermostat Information”.
Write down the date code from that screen. The touch the left arrow at top of display to go to previous screen.
Scroll down until “installer Options” is shown. Touch “installer options” and enter date code.
Select “installer Setup”.
After selecting the correct option for each setting, Touch NEXT at the bottom of the display to advance to the next option.
To see a list of all setup parameters, go to "Installer setup (ISU)" starting on page 16.
To finish setup and save your settings, TOUCH
“Done” in the upper left of display
Fig. 41.
Installer Options
MCR37796
Table 5. Installer Setup (ISU)
ISU # | Installer Setup Name | Settings | Default | Notes
None | Language | English Francais Espanol | Engligh | 
None | Room | Bedroom Living space Other | No defaulted value | In what type of room will this thermostat be installed? These questions are asked for two reasons: Other RedLINK indoor sensors could be used for other spaces in the home. When these sensors are used, the cus- tomer is able to select certain sensors to have priority under certain condi- tions (active rooms based on motion detection, selected rooms based on schedule settings). There may be multiple thermostats in the same location controlled via the app.
None | Room | Bedroom: Guest Bedroom Master Bedroom Add room Living Space: Family room Living Room Rec Room Add room Other: Dining Room Kitchen Basement Hallway Add room Select Room |  | 
None | Units | Fahrenheit Celsius | Fahrenheit | Which temperature scale would you like to use?

## Slide 140
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
17
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
None | RedLINK Devices | Add device Set up later |  | Use to connect RedLINK wireless Accessories. List of compatible RedLINK accessories shown on page 4. Thermostat display will guide you through linking RedLINK accessories to thermostat.
None | Outdoor temperature | None Wired Internet | None | Outdoor temperature is used for balance point lockout, aux heat lockout, frost control, high and low outdoor temperature lockouts for ventilation
2000 | System Type | Conventional Forced Air Heat Heat Pump Radiant Heat None (cool only) | Conventional Forced Air Heat | 
2010 | Equipment Type | Conventional Forced Air Heat Standard Efficiency Gas Forced Air High Efficiency Gas forced air Oil Forced Air Electric Forced Air Hot water Fan Coil Heat Pump Air to Air Geothermal Radiant Heat Hot Water Radiant Heat Steam None (cool only) |  | This ISU is not displayed when ISU 2000 Heating System Type is set to None (Cool Only). Available options depend on “System Type” setting Cycle Rate and Fan Operation automatically default to the correct settings based on the equipment type selected.
2060 | Reversing Valve | O (O/B on Cool) B (O/B on Heat | O (O/B on Cool) | Only displayed if the system type (ISU 2000) is set to Heat Pump
2070 | Cool Stages / Compressor stages | 0, 1, 2 | 1 | 0 setting not available if the system type (ISU 2000) is set to Heat Pump
2071 | Heat stages / Backup heat stages | 0, 1, 2 | 1 | Maximum of 2 Heat Stages for conventional systems. Maximum of 1 Backup Heat Stages for heat pump applications. Note: this is not counting the compressor heat stages on heat pump systems.
2110 | Fan Operation in Heat | Equipment controls fan Thermostat controls fan | Thermostat controls fan | This ISU is only displayed if ISU 2010 is set for Electric Forced Air or Hot Water Fan Coil. The thermostat automatically energizes the fan in heat when running a heat pump. The thermostat automatically allows the system to run the fan in heat when set for gas or oil forced air systems. For radiant systems (excluding hot water fan coil) the thermostat does not energize fan in heat.
2175 | Aux/E terminal control | Drive aux and E together Aux and E Independent | Drive aux and E together | Only displayed if the system type (ISU 2000) is set to Heat Pump) and Backup heat stages (ISU 2071) is set to 1. Change to Aux and E Independent only when you have separate wires to Aux and E terminals on UWP and want the AUX wire energized with heat pump as backup heat and E energized separate of heat pump when switched to em heat mode.

## Slide 141
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
18
ISU # | Installer Setup Name | Settings | Default | Notes
2180 | Backup Heat Type | Electric Forced Air Standard Efficiency Gas Forced Air High Efficiency Gas Forced Air | Electric Forced Air | Only displayed if the system type (ISU 2000) is set to Heat Pump) and Backup heat stages (ISU 2071) is set to 1.
2185 | Emergency Heat Type | Electric Forced Air Standard Efficiency Gas Forced Air High Efficiency Gas Forced Air | Electric Forced Air | Only displayed if the Aux/E terminal control (ISU 2175) is set to “Aux and E Independent”.
2190 | External Fossil Fuel Kit | Thermostat controls Backup Heat External Fossil Fuel kit controls backup heat | Thermostat controls Backup Heat | Not displayed if equipment type (ISU 2000) is set to cool only or cool stages (ISU 2070) is set to 0. This ISU is only displayed when ISU 2000 System Type is Heat Pump and ISU 2180 Backup Heat Type is Standard Efficiency Gas Forced Air or High Efficiency Gas Forced Air.
3000 | Changeover | Manual Automatic | Automatic | Not displayed if equipment type (ISU 2000) is set to cool only or cool stages (ISU 2070) is set to 0.
3015 | Auto Changeover differential | 0 °F-3 °F (0.0 °C-2.5 °C) | 0 | Differential is the minimum number of degrees rise or fall required during off cycle to switch from the last active mode (heat or cool) to the opposite mode when the thermostat is in auto-changeover. Differential is NOT deadband. See Auto Changeover operation on page 38.
3020 | Finish with high cool stage | No Yes | No | This ISU is only displayed when the thermostat is set for 2 cool stages. When set to Yes, then once the thermostat has upstaged to stage 2 cool, this feature keeps the high stage of the cooling equipment running until the desired setpoint is reached.
3021 | Finish with high heat stage | No Yes | No | This ISU is only displayed when the thermostat is set for 2 heat stages. Or a heat pump with 2 compressor stages and/or an aux heat stage. When set to Yes, then once the thermostat has upstaged to stage 2 cool, this feature keeps the high stage of the cooling equipment running until the desired setpoint is reached.
3030 | Cool Differential Stage 2 | Comfort 1.0° F to 3.5° F from setpoint (in 0.5° F increments) set to 2F | Comfort | This ISU is only displayed when the thermostat is set to 2 cool stages. The indoor temperature must rise to the selected differential setting before the thermostat turns on the stage of cooling. For example, if stage 2 is set to 2° F (1.0° C), the indoor temperature must be 2° F (1.0° C) away from the setpoint before stage 2 turns on. When set to Comfort, the thermostat uses the stage of cooling as needed to keep the indoor temperature within 1° F (0.5° C) degree of the setpoint.

## Slide 142
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
19
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
3090 | Backup Heat Differential | Fahrenheit: Comfort, 2.0° F to 15.5° F from setpoint (in 0.5° F increments) Celsius: Comfort, 1.00° C to 7.5° C from setpoint (in 0.5° F increments) Setting depends on customer preference. Select 3F as a default | Comfort if backup heat is electric 2.0F if backup heat is gas furnace. | Only displayed if the system type (ISU 2000) is set to Heat Pump). If ISU 2180 (backup heat type) is set to electric, the default control setting is comfort. If ISU 2180 (backup heat type) is set to Gas furnace, the default control setting is 2F and “Comfort” is not an option. If set to other than “comfort” The indoor temperature must drop to the selected differential setting before the thermostat will turn on backup heat stage 2. For example, if backup heat stage 2 is set to 2°F (1.0° C), the indoor temperature must be 2° F (1.0° C) away from the setpoint before backup heat stage 2 turns on. When set to Comfort, the thermostat will use backup heat stage 2 as needed to keep the indoor temperature within 1° F (0.5° C) degree of the setpoint.
3110 | Backup Heat Upstage Timer | Off (30, 45, 60, 75, 90) minutes (2, 3, 4, 5, 6, 8, 10, 12, 14, 16) hours | Comfort if backup heat is electric 2.0F if backup heat is electric | The Backup Heat Upstage Timer starts when the highest stage of the Heat Pump turns on. Backup heat will be used (if needed) when the timer expires. See “Backup Heat Upstage Timer” on page 40. This ISU is only displayed when Backup Heat Differential is set to 2 F or higher (ISU 3090).
3120 | Compressor Lockout Balance point | Fahrenheit: Off -15° F to 60° F (in 5° F increments) Celsius: Off -26° C to 15.5° C (in varying increments) Setting depends on customer preference. Select 20F as a default | Off | ISU 3120 Compressor Lockout / Balance Point requires a wired outdoor sensor or Internet weather (thermostat connected to Wi-Fi and registered to an account). Default is 40 F if ISU 2010 Heating Equipment Type is Air to Air Heat Pump and ISU 2180 Backup Type is gas or oil forced air. Default is Off if ISU 2010 Heating Equipment Type is Air to Air Heat Pump and ISU 2180 Backup Type is electric forced air. Default is Off if ISU 2010 Heating Equipment Type is Geothermal Heat Pump. See “Heat pump with outdoor temperature lockouts” on page 41.

## Slide 143
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
20
ISU # | Installer Setup Name | Settings | Default | Notes
3120 | Backup Heat Lockout | Fahrenheit: Off 5° F to 65° F (in 5° F increments) Celsius: Off -15.0° F to 18.5° F (in 5° F increments) Note: When both Compressor lockout balance point and Backup Heat Lockout are set to other than “off”, the Backup heat lockout must be at least 5 degrees F above the balance point setting Setting depends on customer preference. Select 40F as a default | Off | This ISU is used to lockout the auxiliary heat when outdoor temperature is above this setting. A 5 degree minimum differential is enforced between balance point and backup heat lockout settings. ISU 3120 Backup Heat Outdoor Temperature Lockout requires a wired outdoor sensor or Internet weather (thermostat connected to Wi-Fi and registered to an account). ISU 3120 defaults to off and is not adjustable unless if ISU 1060 (outdoor Temperature) is set to either Wired or Internet. ISU 3120 is only displayed if ISU 2000 (System Type) is set to Heat Pump, and 2071 (backup heat stages) is set to 1. See “Heat pump with outdoor temperature lockouts” on page 41. NOTE: This is most commonly used when backup heat is electric. For dual fuel systems (Heat pump with gas or oil backup) in which a balance point is used to switch from heat pump to gas or oil furnace, if the outdoor temperature is at the Backup Heat Lockout setting, it is also above the balance point setting. When both balance point and Aux heat lockout are used on dual fuel, if the thermostat is locking out heat pump due to droop or upstage timer, and reaches the Backup Heat Lockout setting, then neither furnace nor heat pump would run during a heat call. Contractors typically only use this setting on dual fuel applications as a warm weather shut down setting for the furnace.
3140 | Cool / Compressor Cycles Per Hour Stage 1 | 1-6 Select 5 as a default | 3 | This ISU is only displayed when ISU 2070 Cool / Compressor Stages is set to 1 or 2 stage. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load. For example, when set to 3 CPH, at a 50% load, the most the system will cycle is 3 times per hour (10 minutes on, 10 minutes off). The system cycles less often when load conditions are less than or greater than a 50% load.
3140 | Cool / Compressor Cycles Per Hour Stage 2 | 1-6 Select 5 as a default | 3 | This ISU is only displayed when ISU 2070 Cool / Compressor Stages is set to 2 stage. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load for the active stage.

## Slide 144
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
21
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
3150 | Heat Cycles Per Hour Stage 1 | 1-12 Select 5 as a default | Default varies based on heating equipment type selected | This ISU is only displayed when ISU 2000 is not seat for heat pump and ISU 2070 Heat Stages is set to 1 or 2 stages. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load. For example, when set to 3 CPH, at a 50% load, the most the system will cycle is 3 times per hour (10 minutes on, 10 minutes off). The system cycles less often when load conditions are less than or greater than a 50% load. The thermostat automatically defaults to the recommended cycle rate based on the heating equipment type that is used. You can change the cycle rate as needed. Defaults for commonly used systems are shown below. Standard Efficiency Gas Forced Air = 5 CPH High Efficiency Gas Forced Air = 3 CPH Oil Forced Air = 5 CPH Electric Forced Air = 9 CPH Hot Water Fan Coil = 3 CPH Hot Water Radiant Heat = 3 CPH Steam = 1 CPH
3150 | Heat Cycles Per Hour Stage 2 | 1-12 Select 5 as a default | Default varies based on heating equipment type selected | This ISU is only displayed when ISU 2071 Heat stages is set to 2 stage for conventional forced air systems. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load for the active stage.
3160 | Backup Heat Cycles per Hour | 1-12 Select 5 as a default | Default varies based on backup heating equipment type selected | This ISU is only displayed when ISU 2000 is set for heat pump and ISU 2071 is set for 1 aux heat stage. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load for the active stage.
3165 | Emergency Heat Cycles per Hour | 1-12 Select 5 as a default | Default varies based on backup heating equipment type selected | This ISU is only displayed when ISU 2175 Aux/E terminal control is set for “Aux and E Independent”. Cycle rate limits the maximum number of times the system can cycle in a 1 hour period measured at a 50% load. For example, when set to 3 CPH, at a 50% load, the most the system will cycle is 3 times per hour (10 minutes on, 10 minutes off). The system cycles less often when load conditions are less than or greater than a 50% load. The thermostat automatically defaults to the recommended cycle rate based on the heating equipment type that is used. You can change the cycle rate as needed. Defaults for commonly used emergency heat shown below. Standard Efficiency Gas Forced Air = 5 CPH High Efficiency Gas Forced Air = 3 CPH Electric Forced Air = 9 CPH

## Slide 145
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
22
ISU # | Installer Setup Name | Settings | Default | Notes
3240 | Minimum Compressor Off Time | Off, 1-5 minutes Select 5 as a default | 5 | The thermostat has a built in compressor protection (minimum off timer) that prevents the compressor from restarting too early after a shutdown. The minimum-off timer is activated after the compressor turns off. If there is a call during the minimum-off timer, the thermostat shows “waiting for equipment” in the display.
3260 | Extended fan run time in cool | 0, 30, 60, 90 seconds, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15 minutes | 0 seconds | After the call for cooling ends, the thermostat keeps the fan on for the selected amount of time for increased efficiency. This may reintroduce humidity into the living space.
3260 | Extended fan run time in heat | 0, 30, 60, 90 seconds, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15 minutes | 0 seconds | After the call for heating ends, the thermostat keeps the fan on for the selected amount of time for increased efficiency.
4090 | Adaptive Intelligent Recovery | No Yes | Yes | No: The system will begin heating or cooling recovery at the scheduled time. Yes: The thermostat will begin heating or cooling recovery early to ensure that the temperature is reached at the scheduled time. The thermostat will adjust the start time of the equipment based on how quickly the scheduled temperature was reached on previous days.
4100 | Minimum Cool Setpoint | 50° F to 99° F * 10.0° C to 36.5° C Select 50 as a default | 50° F (10° C) | The user cannot set the cool setpoint below this level. Thermostat needs to be configured for at least 1 cool/compressor stage. * The minimum cool setpoint cannot be set higher than the maximum cool setpoint. If these settings are the same, the cool setpoint is not adjustable from homescreen.
4100 | Maximum Cool Setpoint | 50° F to 99° F * 31° C to 37° C Select 90 as a default | 90° F (32° C) | The user cannot set the cool setpoint above this level. Thermostat needs to be configured for at least 1 cool/compressor stage. * The maximum cool setpoint cannot be set lower than the minimum cool setpoint. If the max cool and min cool settings are the same, the cool setpoint is not adjustable from homescreen.
4100 | Minimum Heat Setpoint | 40° F to 90° F * 4.5° C to 32° C Select 50 as a default | 50° F (10° C) | The user cannot set the Heat setpoint below this level. Thermostat needs to be configured for at least 1 heat stage. * The minimum heat setpoint cannot be set higher than the maximum heat setpoint or the minimum cool. If these settings are the same, the heat setpoint is not adjustable from homescreen.
4100 | Maximum Heat Setpoint | 40° F to 90° F * 4.5° C to 32° C Select 90 as a default | 90° F (32° C) | The user cannot set the Heat setpoint above this level. Thermostat needs to be configured for at least 1 heat stage. * The maximum heat setpoint cannot be set lower than the minimum heat setpoint. If these settings are the same, the heat setpoint is not adjustable from homescreen.

## Slide 146
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
23
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
4110 | Keypad Lockout | Unlocked Partially locked Fully locked | Unlocked | Unlocked: User has access to all thermostat settings. Partially Locked: User can modify only temperature settings. Fully Locked: User cannot modify any settings
5000 | Is an indoor sensor WIRED to your System? | Indoor air temperature Uncheck box if sensor is not present | Unchecked box (no indoor sensor used) | Select this if a wired indoor sensor is connected to the S terminals. Outdoor wired sensor can be selected at the ISU prior to 2000 for “outdoor temperature”. * You cannot use both a wired outdoor and wired indoor sensor, so if “outdoor temperature” is set to wired sensor, ISU 5000 will not be shown.
5030 | Indoor temperature sensor type | 10K 20K See Sensor type | 10K | Select 10K or 20K based on the sensor installed. Refer to resistance values below: C7189U1005 = 10K ohm See “Installing Wired Indoor Sensor” on page 14 for information wiring multiple indoor sensors.
5040 | Which Sensors will be used for Temperature Control? (Multiple sensors are averaged) | Thermostat Remote Sensor Both | Both | Select whether the internal thermostat sensor or wired sensor(s) are used. If both thermostat and remote sensor are selected, the thermostat would count for 50% of the average and all wired sensors combined would count for the other 50% of the average. This setting does not pertain to the Wireless indoor sensors. You can select which of those are used for control temperature under Menu-Priority from the home screen. See “Installing Wired Indoor Sensor” on page 15 for information wiring multiple indoor sensors.
7000 | Filter Type | None Media | None | 
7020 | Number of air filters | 0-2 0 | 1 | Only shown if ISU 7000 is set to media
7110 | Air filter 1 replacement reminder | Off Run Time: 10, 20, 30 45, 60, 90, 120, 150 days Calendar: 30, 45, 60, 75 days 3, 4, 5, 6, 9, 12, 15 Months Off | Off | Only shown if ISU 7020 is set to 1 or 2
7110 | Air filter 2 replacement reminder | Off Run Time: 10, 20, 30 45, 60, 90, 120, 150 days Calendar: 30, 45, 60, 75 days 3, 4, 5, 6, 9, 12, 15 Months Off | Off | Only shown if ISU 7020 is set to 2

## Slide 147
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
24
ISU # | Installer Setup Name | Settings | Default | Notes
7120 | Clean cell reminder | Off Run Time: 10, 20, 30 45, 60, 90, 120, 150 days Calendar: 30, 45, 60, 75 days 3, 4, 5, 6, 9, 12, 15 Months Off | Off | 
7120 | Clean Prefilter Reminder | Off Run Time: 10, 20, 30 45, 60, 90, 120, 150 days Calendar: 30, 45, 60, 75 days 3, 4, 5, 6, 9, 12, 15 Months Off | Off | 
7120 | Clean Postfilter Reminder | Off Run Time: 10, 20, 30 45, 60, 90, 120, 150 days Calendar: 30, 45, 60, 75 days 3, 4, 5, 6, 9, 12, 15 Months Off | Off | 
8000 | What type of humidifier do you have? | None Steam Bypass or fan powered None | None | 
8050 | Humidification Window Protection | Off On | Off | Requires either wired outdoor sensor or Internet weather (thermostat connected to Wi-Fi and registered to the app). Off: The thermostat controls the humidity level to the user's desired humidity setting. Frost or condensation may appear on windows. On: The thermostat prevents frost or condensation on windows by not allowing the humidity to go above the “Window Limit” when it is controlling the humidifier. The “Window Limit” is based on the current outdoor temperature and the user's window protection setting. The “Window Limit” is displayed on the user's humidification screen. See “Window Protection” on page 35.
8060 | System modes allowing Humidification | Check box on screen for each: Heat Off | Heat | Click boxes on screen to select which system modes allow humidification. If a box is NOT checked, the thermostat will NOT allow humidification to operate in that mode. Heat: Includes Heat, Emergency Heat and Auto. If the system is in Auto mode, the thermostat will allow humidification if the last call was for heat. Off: The thermostat will allow humidification when the system setting is Off. See “Set up Humidification” on page 35.

## Slide 148
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
25
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
8070 | Humidification Control | Humidify Only when Heat is On Humidify Only when Fan is On Humidify on Demand: Thermostat Controls Fan Humidify on Demand: Humidifier Controls Fan | Defaults to Humidify Only when Heat is On when ISU 8000 Humidifier Type is Bypass or Fan Powered. Defaults to Humidify on Demand: Thermostat Controls Fan when ISU 8000 Humidifier Type is Steam | Humidify Only when Heat is On: The thermostat turns on the humidifier only if the heat is currently running. Humidify Only when Fan is On: The thermostat turns on the humidifier only if the fan is currently running. Humidify on Demand - Thermostat Controls Fan: The thermostat turns on the humidifier and the fan when humidification is needed. Humidify on Demand - Humidifier Controls Fan: The thermostat turns on the humidifier when humidification is needed and the humidifier controls the fan.
8100 | Humidifier Pad Replacement Reminder | Off 60 Run Time Days 90 Run Time Days 6 Calendar Months 12 Calendar Months | Off | This ISU is only displayed if ISU 8000 Humidifier Type is Bypass or Fan Powered or none. Run Time Days are not shown if ISU 8000 Humidifier Type is set to None
8100 | Clean Tank/ Water Filter | Off 60 Run Time Days 90 Run Time Days 6 Calendar Months 12 Calendar Months | Off | This ISU is only displayed if ISU 8000 Humidifier Type is Steam.
9000 | What Type of Dehumidifier Equipment Do you Have? | None A/C with Low Speed Fan A/C with High Speed Fan Whole House Dehumidifier | None | See “Dehumidification” on page 36. Whole House Dehumidification and A/C with Low speed Fan only available if not configured to control a Humidifier or Ventilator. A/C with low Speed Fan requires equipment that has a terminal to lower fan speed.
9050 | Dehumidifi- cation Equipment Setup | Normally open Normally closed | Normally Closed | Choose an option appropriate for the type of equipment installed. Normally Open: U contacts will normally be open and will close when the thermostat calls for dehumidification. Normally Closed: U contacts will normally be closed and will open when the thermostat calls for dehumidification.
9070 | Dehumidifi- cation Over- cooling Limit | 0°, 1°, 2°, 3° F (0.5°, 1.0°, 1.5° C) | 3 | This ISU is only displayed when ISU 9000 Dehumidification Equipment is set to A/C with Low Speed Fan or A/C with High Speed Fan. The thermostat uses the cooling system to reduce humidity by lowering the temperature up to 3° F below the current cool setpoint until the desired humidity level is reached. The thermostat keeps the temperature below the cooling setpoint until the desired humidity level is reached. 0° F is only an option when ISU 9000 Dehumidification Equipment is set to A/C with Low Speed Fan.

## Slide 149
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
26
ISU # | Installer Setup Name | Settings | Default | Notes
9120 | System Modes Allowing Dehumidifi- cation | Heat Cool Off | Cool Off Default varies based on heating/ cooling equipment selected | This ISU is only displayed when ISU 9000 Dehumidification Equipment is set to Whole House Dehumidifier. Click boxes on screen to select which system modes allow dehumidification. If a box is NOT checked, the thermostat will NOT allow dehumidification to operate in that mode. Heat: Includes Heat, Emergency Heat and Auto. If the system is in Auto mode, the thermostat will allow dehumidification if the last call was for heat. Cool: Includes Cool and Auto. If the system is in Auto mode, the thermostat will allow dehumidification if the last call was for cool. Off: The thermostat will allow dehumidification when the system setting is Off. See “Dehumidification” on page 34.
9130 | Dehumidifier Fan Control | Thermostat Controls Fan Equipment Controls Fan | Off | This ISU is only displayed when ISU 9000 is set to Whole House Dehumidifier. Thermostat Controls Fan: The thermostat turns on the dehumidifier and the fan when dehumidification is needed. Equipment Controls Fan: The thermostat turns on the dehumidifier when dehumidification is needed. The fan is controlled by the equipment.
9140 | Dehumidifier Lockout | Dehumidifier Allowed when Cool is Running Dehumidifier Not Allowed when Cool is Running | Dehumidifier Allowed when Cool is Running | This ISU is only displayed when ISU 9000 is set to Whole House Dehumidifier. Dehumidifier Allowed when Cool is Running: Dehumidifier can run when the cooling system is on. Dehumidifier Not Allowed when Cool is Running: Dehumidifier can NOT run when the cooling system is on.
9210 | Dehumidifi- cation Filter Replacement Reminder | Off, 30, 60, Calendar Days 3 to 12 Calendar Months (in 1 month increments) Off | Off | 
10000 | Ventilation Type | None ERV/HRV Passive (Fan Only) Fresh Air Damper | None | None: The thermostat does not control ventilation. ERV/HRV: The thermostat controls an Energy Recovery Ventilator or Heat Recovery Ventilator for ventilation. Passive (Fan Only): The thermostat only turns on the fan for ventilation. This assumes the system has a damper that automatically opens whenever the fan runs. Fresh Air Damper: The thermostat turns on the fan and opens a fresh air damper for ventilation.
10050 | Ventilation Control Method | ASHRAE Percent on Time | Ashrae | See “Ventilation Control Methods (ISU 10050)” on page 37.

## Slide 150
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
27
33-00462—03
ISU # | Installer Setup Name | Settings | Default | Notes
10060 | Ventilation Fan Control | Thermostat Controls Fan Equipment Controls Fan if “fresh air damper” or “passive” is selected for ISU 10,000. This setting is not shown and thermostat controls fan by default | Thermostat Controls Fan | Thermostat Controls Fan: The thermostat turns on the ventilation equipment and the fan when ventilation is needed. Equipment Controls Fan: The thermostat turns on the ventilation equipment when ventilation is needed. The fan is controlled by the equipment.
10090 | Number of Bedrooms | 1 to 6 2 | 2 | This ISU is only displayed when ISU10050 Ventilation Control Method is set to ASHRAE.
10090 | Size of house | 1000 to 5000 sq. ft. (in 100 sq. ft. increments) (90 to 460 sq. m.) Input House size | 1000 sq. ft. | This ISU is only displayed when ISU10050 Ventilation Control Method is set to ASHRAE.
10100 | Enter Equipment Ventilation Rate | 30 to 350 CFM (in 5 CFM increments) (850 - 9900 LPM) Input ventilation CFM | 150 CFM | This ISU is only displayed when ISU10050 Ventilation Control Method is set to ASHRAE (Residential only). This is the CFM rating of the ventilation equipment.
10125 | Ventilation Priority | ASHRAE is Priority Lockouts are priority | ASHRAE is Priority | Lockouts are Priority: The thermostat places a priority on lockouts versus the ASHRAE 62.2 ventilation standard. The thermostat will not run ventilation during the following lockout conditions (if configured) unless you manually call for ventilation: Lockout Ventilation during Outdoor Conditions (ISU 10130) Lockout Ventilation during “Sleep” program period. Note: This option is set by the user on the Ventilation screen in the Menu (under options). ASHRAE is Priority: ASHRAE requires additional ventilation following a long off cycle. The thermostat meets the ASHRAE 62.2 ventilation standard by running additional ventilation when outdoor conditions are favorable. If ASHRAE cannot be met when outdoor conditions are favorable, the thermostat will override the outdoor lockouts and run ventilation. When using this option, it is recommended to increase the rate (CFM) of the ventilation equipment to meet the ASHRAE 62.2 ventilation standard in a shorter run time.
10130 | Ventilation Low Temperature Lockout | Off, -20° F to 40° F in 5° F increments. (Off, -29.0° to 4.5°C in varying increments) | Off | Requires either wired outdoor sensor or Internet weather (thermostat connected to Wi-Fi and registered to the app). This ISU is only displayed when ISU 10000 Ventilation Type is set to ERV / HRV or Fresh Air Damper. See “Ventilation — Outdoor Condition Lockouts (ISU 10130)” beginning on page 37.
10130 | Ventilation High Temperature Lockout | Off 80° F to 110° F (in 5° F increments) | Off | 

## Slide 151
T10 PRO SMART THERMOSTAT WITH REDLINK
Table 5. Installer Setup (ISU)
33-00462—03
28
ISU # | Installer Setup Name | Settings | Default | Notes
10130 | Ventilation High Dew Point Lockout | Off 65° F to 85° F in 5° F increments (Off 26.5° C to 43.5° F in varying increments) | Off | Requires Internet weather (thermostat connected to Wi-Fi and registered to the app). Wired outdoor sensor doesn’t enable this setting because wired sensors don’t sense humidity. This ISU is only displayed when ISU 10000 Ventilation Type is set to ERV / HRV or Fresh Air Damper. See “Ventilation — Outdoor Condition Lockouts (ISU 10130)” page 37.
10170 | Ventilator Core Cleaning Reminder | Off 3, 6, 9, 12 Calendar Months | Off | 
10170 | Ventilator Filter Cleaning Reminder | Off 3, 6, 9, 12 Calendar Months | Off | 
11000 | Number of UV Devices | 0, 1, 2 | 0 | Some systems may have two UV devices, one for the A-Coil and another for Air Treatment. A replacement reminder can be setup for each one. Select 0 if no UV devices are installed.
11050 | Replace UV Bulb 1 | Off, 6, 12, 24 Calendar Months | Off | 
11050 | Replace UV Bulb 2 | Off, 6, 12, 24 Calendar Months | Off | 
14010 | Clock Format | 12 Hour Clock 24 Hour Clock | 12 Hour Clock | 
14015 | Daylight Savings Time | No Yes | Yes | Set to Off in areas that do not follow Daylight Saving Time.
14020 | Indoor Temperature Display Offset | -3° F to 3° F in 1° F increments (-1.50° C to 1.50° C in .5° C increments) 0 | 0° F (0.00° C) | 0° F - No difference in displayed temperature and the actual room temperature. The thermostat displays up to 3°F (1.5°C) lower or higher than the actual measured temperature.
14020 | Indoor Humidity Display Offset | -12% to 12% (in 1% increments) 0 | 0° F | 0% - No difference in displayed humidity and the actual room humidity. The thermostat displays up to 12% lower or higher than the actual measured humidity.
15000 | Dealer information | Company Phone Website Email Contractor Pro - number |  | Touch each individual category to enter the information. If an alert or notification appears on the screen, the customer will be shown the dealer information so they know who to contact. Enter your company’s Contractor PRO account number to receive bonus points for every T10 Pro Smart thermostat you install. Your account number is an 8 digit number which includes a leading zero (example 01234567).

## Slide 152
www.ecoer.com
Air Handler Unit Installation Instruction
12/20
System Types List
Type | Descriptions | Application | Required Terminals
0 | Cool only | ESI (AC only) + Air Handler | C, RC, Y1, G
3 | Cool only | ESI + Air Handler | C, RC, Y1, O, G
6 | 1H/1C | ESI + Air Handler | C, RH, Y1, O, G, *W2
8 | 1H/1C | ESI + Air Handler | See details on EST Install and User Guide
9 | 1H/2C (G/G2) | ESI + E series Air Handler | 
10 (Default) | 2H/1C | ESI + Air Handler ESI + Gas Furnace | 
11 | 2H/2C (G/G2) | ESI + E series Air Handler | 
12 | Cool only (G/G2) | AC only + E series Air Handler | 
13 | Cool only (G/G2) + W2 |  | 
REMARKS:
No output from EST01 at O terminal if select Type 8 ~ 13.
Type 6 can be used as a BACKUP for heat pump (Normal O signal output) application without two-stage fan control in cooling.
ESI- Ecoer Smart Inverter condensing unit * means optional connection
4.3 Grounding
WARNING
The unit must be permanently grounded.
Failure to do so can result in electrical shock causing personal injury or death.

## Slide 153
www.ecoer.com
Air Handler Unit Installation Instruction
13/20
4.5 Electric Heat Data
Kit Model | Model Number | Electric Heat (kW) | MIN. Circuit Ampacity |  | MAX. Fuse or Breaker (HACR) Ampacity |  | Fan speed |  |  |  | 
 |  |  | 240 | 208 | 240 | 208 | 1 | 2 | 3 | 4 | 5
E-EHK05 | 24 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | × | ● | ● | ●
E-EHK05 | 36 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | × | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK05 | 48 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | ● | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK20 |  | 10+10 | 49+49 | 43+43 | 60+60 | 50+50 | × | × | × | ● | ●
E-EHK05 | 60 | 5 | 25 | 22 | 30 | 25 | × | ● | ● | ● | ●
E-EHK10 |  | 10 | 49 | 43 | 60 | 50 | × | ● | ● | ● | ●
E-EHK15 |  | 5+10 | 25+49 | 22+43 | 30+60 | 25+50 | × | × | ● | ● | ●
E-EHK20 |  | 10+10 | 49+49 | 43+43 | 60+60 | 50+50 | × | × | × | ● | ●
means available ×means unavailable
Electric heat kits are suitable for air handler multiple position installation.
Safety Cautions
All electric work must be performed by qualified personnel.
EHK series is designed and approved to be installed in the EAHATN series air handlers.
Check the EHK label to confirm suitable kW selection based on room load under lowest temperature ambient.
Inspect all porcelain in insulators for breakage and the intact of heater element wire. Contact local distributor immediately if thereis any occurred damage.
Warning
Disconnect all external power supplies before performing installation and servicing. Turn off accessory heater power switch if applicable. Failure to do so may cause serious injury.
EHK must be properly grounded and use copper supplywires.
Make sure to follow national electric code and local regulations.
When installing it in an enclosed area such as a garage, heater elements should have a minimum clearance of 18’’ from the floor to insure theproper ventilation.

## Slide 154
www.ecoer.com
Air Handler Unit Installation Instruction 14/20
4.6 Electric Heat Installation Guide
STEP 1. Unfasten 4 screws to take away the blower access panel of the air handler.
STEP 2. Remove cover plate actual requirement.
based on
STEP 3. Slide the kit into the duct and fasten the element (e.g. attachment and wires).
STEP 4. Install the circuit breaker into the mounting rail. Knock off the reserved cover for breaker in blower access panel prior to put it back to the unit.
3-1
3-2
4
Connect to CN6
Power Supply
1
Knock off this cover for circuit breaker
2

## Slide 155
Air Handler Unit Installation Instruction 15/20 www.ecoer.com
WARNING
Disconnect all power to unit before installing or servicing. More than one disconnect switch may be required to de-energize the equipment. Hazardous voltage can cause severe personal injury or death.
Figure 4-3 Wiring diagram for electric heat

## Slide 156
Air Handler Unit Installation Instruction 16/20 www.ecoer.com
5. Airflow Performance
Airflow performance data is based on cooling performance with a coil and no filter in place. Check the
Performance table for appropriate unit size selection. External static pressure should stay within the minimum and maximum limits shown in the table below in order to ensure proper.
Model Number | Motor Speed |  | CFM (Watts) |  |  |  |  |  |  |  |  | 
 |  |  | External Static Pressure-Inches W.C.[KPa] |  |  |  |  |  |  |  |  | 
 |  |  | 0 [0] | 0.1 [.02] | 0.16 [.04] | 0.2 [.05] | 0.3 [.07] | 0.4 [.10] | 0.5 [.12] | 0.6 [.15] | 0.7 [.17] | 0.8 [.20]
24 | Tap (5) | SCFM | 1062 | 1031 | 998 | 981 | 947 | 901 | 869 | 823 | 789 | 742
 |  | Watts | 184 | 195 | 201 | 203 | 213 | 222 | 228 | 238 | 242 | 252
 | Tap (4) | SCFM | 959 | 921 | 890 | 873 | 836 | 786 | 751 | 706 | 677 | 622
 |  | Watts | 138 | 145 | 152 | 156 | 162 | 171 | 178 | 188 | 196 | 204
 | Tap (3)- factory | SCFM | 855 | 825 | 790 | 769 | 733 | 679 | 646 | 595 | 560 | 494
 |  | Watts | 101 | 111 | 118 | 120 | 126 | 134 | 141 | 151 | 156 | 166
 | Tap (2) | SCFM | 777 | 750 | 712 | 692 | 656 | 599 | 566 | 498 | 466 | 412
 |  | Watts | 80 | 89 | 96 | 98 | 104 | 113 | 119 | 127 | 135 | 145
 | Tap (1) | SCFM | 694 | 663 | 620 | 599 | 562 | 499 | 455 | 390 | --- | ---
 |  | Watts | 60 | 68 | 74 | 76 | 82 | 89 | 95 | 104 | --- | ---
36 | Tap (5) | SCFM | 1455 | 1409 | 1374 | 1355 | 1320 | 1266 | 1229 | 1173 | 1126 | 956
 |  | Watts | 293 | 300 | 306 | 309 | 316 | 326 | 331 | 338 | 346 | 370
 | Tap (4) | SCFM | 1350 | 1302 | 1264 | 1242 | 1206 | 1145 | 1104 | 1038 | 897 | 824
 |  | Watts | 238 | 243 | 254 | 257 | 260 | 271 | 277 | 286 | 303 | 308
 | Tap (3)- factory | SCFM | 1328 | 1281 | 1234 | 1215 | 1179 | 1118 | 1073 | 1007 | 862 | 798
 |  | Watts | 226 | 232 | 239 | 242 | 250 | 259 | 264 | 278 | 292 | 298
 | Tap (2) | SCFM | 1235 | 1171 | 1130 | 1108 | 1062 | 1002 | 955 | 824 | 752 | 713
 |  | Watts | 185 | 189 | 196 | 199 | 205 | 214 | 221 | 238 | 245 | 248
 | Tap (1) | SCFM | 1146 | 1091 | 1044 | 1022 | 982 | 908 | 823 | 748 | 708 | ---
 |  | Watts | 150 | 156 | 163 | 167 | 174 | 184 | 196 | 202 | 207 | ---
48 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327
60 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327
Shaded boxes represent airflow outside the required 300-450cfm/ton.
NOTES:
Airflow based upon cooling performance at 230V with no electric heat and no filter. Airflow at 208V is approximately the same as 230V because the multi-tap ECM motor is a constant torque motor. The torque doesn’t drop off at the speeds in which the motor operates.
G2 signal occupies Tap (1) reserved for Ecoer thermostat (EST01) to get even better dehumidification control in cooling.
Model Number | Motor Speed |  |  |  |  |  |  |  |  |  |  | 
 |  |  | External Static Pressure-Inches W.C.[KPa] |  |  |  |  |  |  |  |  | 
 |  |  | 0 [0] | 0.1 [.02] | 0.16 [.04] | 0.2 [.05] | 0.3 [.07] | 0.4 [.10] | 0.5 [.12] | 0.6 [.15] | 0.7 [.17] | 0.8 [.20]
24 | Tap (5) | SCFM | 1062 | 1031 | 998 | 981 | 947 | 901 | 869 | 823 | 789 | 742
 |  | Watts | 184 | 195 | 201 | 203 | 213 | 222 | 228 | 238 | 242 | 252
 | Tap (4) | SCFM | 959 | 921 | 890 | 873 | 836 | 786 | 751 | 706 | 677 | 622
 |  | Watts | 138 | 145 | 152 | 156 | 162 | 171 | 178 | 188 | 196 | 204
 | Tap (3)- factory | SCFM | 855 | 825 | 790 | 769 | 733 | 679 | 646 | 595 | 560 | 494
 |  | Watts | 101 | 111 | 118 | 120 | 126 | 134 | 141 | 151 | 156 | 166
 | Tap (2) | SCFM | 777 | 750 | 712 | 692 | 656 | 599 | 566 | 498 | 466 | 412
 |  | Watts | 80 | 89 | 96 | 98 | 104 | 113 | 119 | 127 | 135 | 145
 | Tap (1) | SCFM | 694 | 663 | 620 | 599 | 562 | 499 | 455 | 390 | --- | ---
 |  | Watts | 60 | 68 | 74 | 76 | 82 | 89 | 95 | 104 | --- | ---
36 | Tap (5) | SCFM | 1455 | 1409 | 1374 | 1355 | 1320 | 1266 | 1229 | 1173 | 1126 | 956
 |  | Watts | 293 | 300 | 306 | 309 | 316 | 326 | 331 | 338 | 346 | 370
 | Tap (4) | SCFM | 1350 | 1302 | 1264 | 1242 | 1206 | 1145 | 1104 | 1038 | 897 | 824
 |  | Watts | 238 | 243 | 254 | 257 | 260 | 271 | 277 | 286 | 303 | 308
 | Tap (3)- factory | SCFM | 1328 | 1281 | 1234 | 1215 | 1179 | 1118 | 1073 | 1007 | 862 | 798
 |  | Watts | 226 | 232 | 239 | 242 | 250 | 259 | 264 | 278 | 292 | 298
 | Tap (2) | SCFM | 1235 | 1171 | 1130 | 1108 | 1062 | 1002 | 955 | 824 | 752 | 713
 |  | Watts | 185 | 189 | 196 | 199 | 205 | 214 | 221 | 238 | 245 | 248
 | Tap (1) | SCFM | 1146 | 1091 | 1044 | 1022 | 982 | 908 | 823 | 748 | 708 | ---
 |  | Watts | 150 | 156 | 163 | 167 | 174 | 184 | 196 | 202 | 207 | ---
48 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327
60 | Tap (5) | SCFM | 2144 | 2106 | 2072 | 2052 | 2015 | 1962 | 1924 | 1864 | 1823 | 1768
 |  | Watts | 627 | 632 | 639 | 643 | 649 | 661 | 670 | 681 | 684 | 696
 | Tap (4) | SCFM | 1999 | 1966 | 1933 | 1915 | 1875 | 1819 | 1775 | 1713 | 1672 | 1582
 |  | Watts | 510 | 520 | 529 | 536 | 540 | 551 | 555 | 567 | 571 | 588
 | Tap (3)- factory | SCFM | 1788 | 1746 | 1714 | 1695 | 1660 | 1606 | 1565 | 1499 | 1452 | 1355
 |  | Watts | 367 | 374 | 389 | 393 | 404 | 422 | 429 | 440 | 449 | 458
 | Tap (2) | SCFM | 1633 | 1596 | 1564 | 1554 | 1514 | 1467 | 1424 | 1342 | 1290 | 1231
 |  | Watts | 292 | 300 | 311 | 318 | 329 | 343 | 354 | 376 | 382 | 391
 | Tap (1) | SCFM | 1504 | 1468 | 1428 | 1408 | 1362 | 1298 | 1244 | 1182 | 1160 | 1081
 |  | Watts | 228 | 242 | 250 | 255 | 264 | 279 | 291 | 309 | 318 | 327

## Slide 157
Air Handler Unit Installation Instruction 17/20 www.ecoer.com
This air handler keeps the selected TAP all the way in heating mode, but switches between the selected TAP and the lowest TAP (1) controlled by G and G2 signal sending from Ecoer thermostat (EST01). G signal will be turned OFF and G2 signal will be turned ON if the difference between indoor temp. and desired one is < 3F.
Indoor motor has 90 seconds delay after G/G2 inputs are gone no matter it runs cooling or heating.
The air distribution system has the greatest effect on airflow. For this reason, the contractor should use only industry-recognized procedures to finish ductwork.
Heat pump systems require a specified airflow. Each ton of cooling requires between 300 and 450 cubic feet per minute (CFM). Duct design and construction should be carefully done. System performance can be lowered dramatically through bad planning or workmanship.
Air supply diffusers must be selected and located carefully. They must be sized and positioned to deliver treated air along the perimeter of the space. Return air grilles must be properly sized to carry air back to the blower as well. Failure to follow these may cause abnormal noise and drafts.
The installers should balance the air distribution system to ensure proper quiet airflow to all rooms in the home. This ensures a comfortable living space. An air velocity meter or airflow hood can give a reading of system CFM.
Temp.
G Signal
ON
OFF
ON
ON
G2 Signal OFF
TAPselected in the job site
TAP (1)

## Slide 158
Air Handler Unit Installation Instruction 18/20 www.ecoer.com
6. Ductwork
Field ductwork must comply with the National Fire Protection Association NFPA 90A, NFPA 90B and any applicable local ordinance.
WARNING
Do not, under any circumstances, connect return ductwork to any other heat producing device such as fireplace insert, stove, etc. Unauthorized use of such devices may result in fire, carbon monoxide poisoning, explosion, personal injury or property damage.
Sheet metal ductwork run in unconditioned spaces must be insulated and covered with a vapor barrier. Fibrous ductwork may be used if constructed and installed in accordance with SMACNA Construction Standard on Fibrous Glass Ducts. Ductwork must comply with National Fire Protection Association as tested by U/L Standard 181 for Class I Air Ducts. Check local codes for requirements on ductwork and insulation.
Duct system must be designed within the range of external static pressure the unit is designed to operate against. It is important that the system airflow be adequate. Make sure supply and return ductwork, grilles, special filters, accessories, etc. are accounted for in total flow resistance. Refer to the airflow performance table in this manual.
Design the duct system in accordance with “ACCA” Manual “D” Design for Residential Winter and Summer Air Conditioning and Equipment Selection. Latest editions are available from: “ACCA” Air Conditioning Contractors of America, 1513 16th Street, N.W., Washington, D.C. 20036. If duct system incorporates flexible air duct, be sure that the pressure drop Information (straight length plus all turns) shown in “ACCA” Manual “D” is accounted for insystem.
Supply plenum is attached to the 3/4” duct flanges supplied with the unit. Attach flanges around the blower outlet.
Secure the supply and return ductwork to the unit flanges, using proper fasteners for the type of duct used and tape the duct-to-unit joint as required to prevent air leaks.
IMPORTANT
If an elbow is included in the plenum close to the unit, it must not be smaller than the dimensions of the supply duct flange on the unit.
The front flange on the return duct connected to the blower casing must not be screwed into the area where the power wiring is located. Drills or sharp screw points can damage insulation on wires located inside unit.

## Slide 159
Air Handler Unit Installation Instruction 19/20 www.ecoer.com
7. Pipe Connections
Keep the coil connections sealed until refrigerant connections are made. Refer to condensing unit installation instructions for details on pipe size and insulation.
Coil is shipped with Nitrogen. Evacuate the system before charging with refrigerant.
Make sure the refrigerant pipes layout do not block service access.
Purge the refrigerant pipes and indoor coil with dry nitrogen while brazing.
Use a wet rag or an approved heat paste to protect the TXV sensing bulb during the brazing process.
Condensate Drain Connection
Use a thin layer of Teflon paste, silicone or Teflon tape when making drain fitting connections.
Do not over tighten fittings resulting in splitting pipe connections on the drain pan.
Figure 7-1 Condensate drain trap
Make sure the drain pipes layout do not block service access. Minimum clearance of 24 inches is required for filter, coil or blower removal and serviceaccess.
Ensure the unit is level or pitched slightly toward primary drain connection so that water will drain smoothly from the pan. All horizontal drain pipes must be pitched downward away from the unit a minimum of 1/8” per footof line to ensure proper drainage.
Do not reduce drain pipe size less than connection size provided on condensate drain pan.
Do not connect condensate drain pipe to a closed or open sewer pipe.
The drain pipe should be insulated where necessary to prevent sweating and damage due to condensate forming on the outside surfaceof the line.
Make provisions for disconnecting and cleaning of the primary drain pipe if it become necessary. Install a 3- inch trap in the primary drain pipe as close as possible to the unit. Make sure that the top of the trap is below connection to the drain pan to allow complete drainage of pan.
Auxiliary drain pipe should be connected to a place where it will be noticeable. Homeowner should be warned that a problem exists if water begins running from the auxiliary drain pipe.
Test condensate drain pan and drain pipe after installation is complete. Pour enough water into drain pan, make sure that the drain pan is draining completely, no leaks are found in drain pipe fittings, and no water is draining from the termination of theprimary drain pipe.

## Slide 160
Air Handler Unit Installation Instruction 20/20 www.ecoer.com
8. Air Filter
Filter application and replacement are critical to airflow, which may affect the heating and cooling system performance. Reduced airflow can shorten the life of the system’s major components, such as motor, heat relays, evaporator coil or compressor. Units should be sized for a maximum of 300 feet/min. air velocity or what is recommended for the filter type installed.
Ensure the air flow is in the range of 300~450CFM if adding high efficiency filters or electronic air filtration systems. Note that the overall performance and efficiency of the unit will be reduced because of pressure drop by filters.
IMPORTANT
Do not double filter the return air duct.
Do not filter the supply air duct which will change the performance of the unit and reduce airflow .
WARNING
Do not operate the system without filters. A portion of the dust suspended in the air may temporarily lodge in the duct. Any circulated dust particles could be heated and charred by contact with the air handler elements.
This residue could soil ceilings, walls, drapes, carpets and other articles in the house. Soot damage may occur without filters in place when certain types of candles, oil lamps or standing pilots are burned.
Air Filter Clean/Replacement
Remove bolts to take the filter cover away.
Hold the edge of the air filter and extract it out .
Clean the air filter or use a new one to replace.
NOTE: AIR FILTER IS NOT FACTORY INSTALLED.
Figure 8-1 Filter installation and clean
Model Number | Dimensions (in.) |  |  |  |  | 
 | Filter Size | W | D | H | A | B
24 / 36 | 19x20 (19x19) | 19-3/4 | 21 | 1 | 16 | 13-7/8
48 / 60 | 23x20 | 23-1/4 | 21 | 1 | 16 | 15-1/4

## Slide 161
Air Handler Unit Installation Instruction 21/20 www.ecoer.com
9. TXV Adjustment
To keep the best Ecoer Smart Inverter(ESI) systems’ performance and reliability, be sure liquid line sub- cooling(SC) and compressor suction superheat(SH) meet our requirements.
Target SC and SH in cooling
If the LED displays “--” in AUTO charge mode for more than 20 minutes, stop charging and use a wrench to
clockwise the TXV to ensure SH is no less than 7゜F.
In case that the cooling performance is abnormal due to improper superheat (i.e. SH >20 ゜ F). Adjust the system according to
  Activate AUTO charge mode from outdoor condensing unit to fix compressor frequency(RPS) by press BS4 for 5 seconds on PCB. Run the system for 15~20 minutes and check refrigerant coefficient number from LED display or ESS Pro App, add refrigerant until you get 0.6.
  Open the front panel of the air handler unit, then use a wrench to counterclockwise the TXV until SH
≤ 20゜F. This will make more refrigerant flow into indoor coil for better cooling performance.
NOTE: Maintain a minimum of 5 minutes’ operation after every refrigerant amount or TXV opening adjustment, then check live SC and SH from Ecoer Smart Service Mobile App.
Remember:
Put back the panel after TXV adjusted.
7~20゜F
6~18゜F
SC SH

## Slide 163
Air Handler Unit Installation Instruction 22/20 www.ecoer.com
©2017-2019 ECOER INC.
3900 Jermantown Rd, Suite 150, Fairfax, VA 22030
Tel: 703-348-2538
www.ecoer.com
Manufacturer reserves the right to change specifications or designs without notice.